## Configuration
Configuration
PEL Transfer, Version 2.8.15973
Instrument ID
PEL model | PEL103
PEL serial number | 176761WEH
PEL name | PEL103-176761WEH
PEL location | Office
Firmware DSP version | 1.28
Firmware microprocessor version | 1.20
Hardware version | D.D
Measurement configuration and status
Aggregation period | 10 min
Electrical hook-up | 3-phase 4-wire Y
Nominal frequency | Auto
Primary nominal voltage | - - -
Secondary nominal voltage | - - -
Current sensor I1 | MA193/MA194/A193/A196
Current sensor I2 | MA193/MA194/A193/A196
Current sensor I3 | MA193/MA194/A193/A196
Line flexible sensor range | 2,000 A
Line flexible sensor wraps | 1

## Summary
Summary
| V1 (10 min) | V2 (10 min) | V3 (10 min) | U12 (10 min) | U23 (10 min) | U31 (10 min) | I1 (10 min) | I2 (10 min) | I3 (10 min) | IN (10 min) | V1ᴄꜰ (10 min) | V2ᴄꜰ (10 min) | V3ᴄꜰ (10 min) | I1ᴄꜰ (10 min) | I2ᴄꜰ (10 min) | I3ᴄꜰ (10 min) | F (Hz) (10 min) | P1 (10 min) | P2 (10 min) | P3 (10 min) | PT (10 min) | P1- (10 min) | P2- (10 min) | P3- (10 min) | PT- (10 min) | P1+ (10 min) | P2+ (10 min) | P3+ (10 min) | PT+ (10 min) | Q1 (10 min) | Q2 (10 min) | Q3 (10 min) | QT (10 min) | Q1- (10 min) | Q2- (10 min) | Q3- (10 min) | QT- (10 min) | Q1+ (10 min) | Q2+ (10 min) | Q3+ (10 min) | QT+ (10 min) | S1 (10 min) | S2 (10 min) | S3 (10 min) | ST (10 min) | PF1- (10 min) | PF2- (10 min) | PF3- (10 min) | PFT- (10 min) | PF1+ (10 min) | PF2+ (10 min) | PF3+ (10 min) | PFT+ (10 min) | Cos φ1- (10 min) | Cos φ2- (10 min) | Cos φ3- (10 min) | Cos φT- (10 min) | Cos φ1+ (10 min) | Cos φ2+ (10 min) | Cos φ3+ (10 min) | Cos φT+ (10 min) | Tan Φ- (10 min) | Tan Φ+ (10 min) | V1ᴛʜᴅ (10 min) | V2ᴛʜᴅ (10 min) | V3ᴛʜᴅ (10 min) | U12ᴛʜᴅ (10 min) | U23ᴛʜᴅ (10 min) | U31ᴛʜᴅ (10 min) | I1ᴛʜᴅ (10 min) | I2ᴛʜᴅ (10 min) | I3ᴛʜᴅ (10 min) | INᴛʜᴅ (10 min)
| V | V | V | V | V | V | A | A | A | A | [6 empty] | Hz | W | W | W | W | W | W | W | W | W | W | W | W | var | var | var | var | var | var | var | var | var | var | var | var | VA | VA | VA | VA | [18 empty] | % | % | % | % | % | % | % | % | % | %
2026-06-18 14:45 | 241.65 | 243.5 | 240.88 | 418.78 | 418.85 | 419.82 | 1.9721 | 0 | 2.2878 | 0 | 1.438 | 1.443 | 1.429 | 1.977 | # # # | 1.85 | 49.96 | -114 | 0 | 424 | 311 | 114 | 0 | - - - | - - - | - - - | 0 | 424 | 311 | 462 | - - - | 350 | 812 | -462 | - - - | - - - | - - - | - - - | - - - | 350 | 812 | 477 | 0 | 551 | 1028 | -0.24 | # # # | # # # | # # # | # # # | # # # | 0.771 | 0.303 | # # # | # # # | # # # | # # # | # # # | # # # | 0.837 | 0.837 | # # # | 2.617 | 1.73 | 1.58 | 1.46 | 1.52 | 1.46 | 1.42 | 33.82 | # # # | 29.27 | # # #
2026-06-18 14:55 | 240.09 | 241.95 | 240.27 | 416.52 | 416.9 | 417.61 | 40.7823 | 40.2818 | 44.0125 | 1.9479 | 1.433 | 1.436 | 1.429 | 1.747 | 1.649 | 1.688 | 49.98 | 8915 | 8972 | 9844 | 27731 | 5 | - - - | - - - | - - - | 8920 | 8972 | 9844 | 27731 | 3425 | 3175 | 3204 | 9843 | -20 | - - - | - - - | - - - | 3445 | 3175 | 3204 | 9843 | 9587 | 9521 | 10356 | 29464 | -0.968 | # # # | # # # | # # # | 0.935 | 0.945 | 0.945 | 0.941 | # # # | # # # | # # # | # # # | 0.989 | 0.999 | 0.99 | 0.993 | # # # | 0.448 | 2.07 | 1.78 | 1.68 | 1.81 | 1.66 | 1.76 | 30.72 | 29.96 | 29.18 | 387.1
2026-06-18 15:05 | 241.42 | 242.53 | 240.9 | 418.12 | 418.09 | 419.21 | 15.8402 | 15.4808 | 17.1247 | 0.9306 | 1.437 | 1.439 | 1.43 | 1.973 | 0.259 | 1.829 | 49.97 | 1217 | 1326 | 1839 | 4382 | 107 | - - - | - - - | - - - | 1324 | 1326 | 1839 | 4382 | 139 | 488 | 792 | 2195 | -388 | - - - | - - - | - - - | 527 | 488 | 792 | 2195 | 1830 | 1414 | 2026 | 5270 | -0.371 | # # # | # # # | # # # | 0.99 | 0.991 | 0.808 | 0.832 | # # # | # # # | # # # | # # # | 0.997 | 0.999 | 0.869 | 0.955 | # # # | 2.214 | 1.55 | 1.48 | 1.36 | 1.38 | 1.33 | 1.3 | 33.6 | 5 | 29.15 | 50.05
2026-06-18 15:15 | 238.75 | 240.89 | 239.04 | 414.39 | 414.84 | 415.49 | 36.309 | 35.8403 | 39.0051 | 1.6028 | 1.436 | 1.439 | 1.427 | 1.788 | 1.192 | 1.712 | 49.98 | 6715 | 6803 | 7534 | 21051 | 39 | - - - | - - - | - - - | 6754 | 6803 | 7534 | 21051 | 2428 | 2383 | 2486 | 7567 | -135 | - - - | - - - | - - - | 2563 | 2383 | 2486 | 7567 | 7368 | 7212 | 7944 | 22524 | -0.785 | # # # | # # # | # # # | 0.955 | 0.961 | 0.909 | 0.935 | # # # | # # # | # # # | # # # | 0.995 | 0.998 | 0.962 | 0.985 | # # # | 0.996 | 2.08 | 1.7 | 1.62 | 1.78 | 1.58 | 1.73 | 31.45 | 21.96 | 28.4 | 136.75
2026-06-18 15:25 | 239.78 | 241.31 | 239.7 | 415.68 | 415.89 | 416.82 | 28.6966 | 28.1587 | 30.867 | 1.4545 | 1.441 | 1.443 | 1.43 | 1.9 | 0.778 | 1.766 | 50.01 | 4181 | 4246 | 4910 | 13337 | 67 | - - - | - - - | - - - | 4248 | 4246 | 4910 | 13337 | 1403 | 1523 | 1733 | 5138 | -239 | - - - | - - - | - - - | 1642 | 1523 | 1733 | 5138 | 4803 | 4512 | 5225 | 14540 | -0.592 | -0.998 | # # # | # # # | 0.971 | 0.974 | 0.862 | 0.917 | # # # | # # # | # # # | # # # | 0.997 | 0.998 | 0.91 | 0.968 | # # # | 1.45 | 1.64 | 1.62 | 1.46 | 1.52 | 1.44 | 1.43 | 33.99 | 14.51 | 26.65 | 122.75
2026-06-18 15:35 | 241.86 | 243.34 | 241.65 | 419.18 | 419.39 | 420.31 | 31.9388 | 31.7312 | 34.5552 | 1.9309 | 1.437 | 1.438 | 1.43 | 1.836 | 0.828 | 1.708 | 50.01 | 5029 | 5168 | 5870 | 16067 | 77 | - - - | - - - | - - - | 5106 | 5168 | 5870 | 16067 | 1693 | 1769 | 1931 | 5841 | -224 | - - - | - - - | - - - | 1917 | 1769 | 1931 | 5841 | 5695 | 5465 | 6194 | 17354 | -0.662 | # # # | # # # | # # # | 0.967 | 0.972 | 0.89 | 0.926 | # # # | # # # | # # # | # # # | 0.993 | 0.999 | 0.94 | 0.977 | # # # | 1.363 | 2 | 1.61 | 1.53 | 1.65 | 1.5 | 1.64 | 31.62 | 14.78 | 29.08 | 107.4
2026-06-18 15:45 | 242.76 | 244.2 | 242.52 | 420.71 | 420.86 | 421.86 | 40.5795 | 40.0351 | 43.3666 | 1.522 | 1.44 | 1.439 | 1.429 | 1.808 | 1.167 | 1.742 | 49.95 | 7610 | 7659 | 8424 | 23694 | 31 | - - - | - - - | - - - | 7641 | 7659 | 8424 | 23694 | 2681 | 2635 | 2766 | 8386 | -152 | - - - | - - - | - - - | 2833 | 2635 | 2766 | 8386 | 8305 | 8101 | 8884 | 25290 | -0.751 | -1 | # # # | # # # | 0.957 | 0.963 | 0.882 | 0.937 | # # # | # # # | # # # | # # # | 0.993 | 0.998 | 0.936 | 0.976 | # # # | 1.114 | 1.7 | 1.5 | 1.42 | 1.48 | 1.34 | 1.45 | 33.4 | 21.41 | 28.85 | 135.45
2026-06-18 15:55 | 244.35 | 245.19 | 243.67 | 422.95 | 422.88 | 424.06 | 22.1338 | 21.878 | 23.5082 | 0.9323 | 1.434 | 1.438 | 1.428 | 1.96 | 0.316 | 1.857 | 49.97 | 2048 | 2166 | 2687 | 6901 | 107 | - - - | - - - | - - - | 2155 | 2166 | 2687 | 6901 | 408 | 757 | 1049 | 3022 | -404 | - - - | - - - | - - - | 812 | 757 | 1049 | 3022 | 2725 | 2298 | 2914 | 7938 | -0.394 | # # # | # # # | # # # | 0.987 | 0.989 | 0.806 | 0.869 | # # # | # # # | # # # | # # # | 0.997 | 1 | 0.87 | 0.956 | # # # | 2.295 | 1.73 | 1.57 | 1.42 | 1.5 | 1.42 | 1.47 | 34.5 | 5.61 | 30.93 | 68.85
2026-06-18 16:05 | 244.07 | 245.14 | 243.39 | 422.58 | 422.64 | 423.62 | 50.7897 | 50.1544 | 53.7602 | 1.7809 | 1.439 | 1.441 | 1.436 | 1.742 | 1.722 | 1.695 | 49.96 | 11610 | 11606 | 12447 | 35664 | - - - | - - - | - - - | - - - | 11610 | 11606 | 12447 | 35664 | 4334 | 3992 | 4023 | 12348 | - - - | - - - | - - - | - - - | 4334 | 3992 | 4023 | 12348 | 12393 | 12291 | 13082 | 37766 | # # # | # # # | # # # | # # # | 0.938 | 0.946 | 0.952 | 0.944 | # # # | # # # | # # # | # # # | 0.993 | 1 | 0.997 | 0.997 | # # # | 0.346 | 2.51 | 2.2 | 1.93 | 2.26 | 2.03 | 2.1 | 29.77 | 30.83 | 28.98 | 320.67
2026-06-18 16:15 | 245.21 | 245.55 | 244.09 | 424.06 | 423.63 | 425.05 | 6.1294 | 5.659 | 6.5103 | 0.1627 | 1.426 | 1.428 | 1.422 | 2.036 | 0.023 | 1.949 | 49.96 | 38 | 142 | 558 | 737 | 105 | - - - | - - - | - - - | 143 | 142 | 558 | 737 | -448 | 52 | 443 | 1052 | -503 | - - - | - - - | - - - | 55 | 52 | 443 | 1052 | 668 | 152 | 726 | 1546 | -0.214 | # # # | # # # | # # # | 0.999 | 0.999 | 0.723 | 0.477 | # # # | # # # | # # # | # # # | 0.998 | 1 | 0.788 | 0.929 | # # # | 2.955 | 1.13 | 1.14 | 1.11 | 0.95 | 1.01 | 0.96 | 36.44 | 1.02 | 32.93 | 3.01
2026-06-18 16:25 | 244.83 | 245.37 | 243.89 | 423.52 | 423.28 | 424.63 | 39.1298 | 38.4241 | 41.3735 | 1.1188 | 1.429 | 1.432 | 1.426 | 1.85 | 0.97 | 1.79 | 49.93 | 6747 | 6746 | 7441 | 20935 | 46 | - - - | - - - | - - - | 6793 | 6746 | 7441 | 20935 | 2272 | 1951 | 2476 | 7133 | -217 | - - - | - - - | - - - | 2489 | 1951 | 2476 | 7133 | 7459 | 7132 | 7869 | 22460 | -0.661 | # # # | # # # | # # # | 0.965 | 0.974 | 0.853 | 0.932 | # # # | # # # | # # # | # # # | 0.996 | 0.998 | 0.91 | 0.968 | # # # | 1.467 | 1.58 | 1.51 | 1.4 | 1.41 | 1.35 | 1.37 | 33.26 | 17.73 | 29.99 | 128.88
2026-06-18 16:35 | 245.1 | 245.75 | 244.18 | 424.08 | 423.86 | 425.12 | 40.5279 | 39.8041 | 42.8106 | 1.1803 | 1.428 | 1.433 | 1.425 | 1.853 | 1.082 | 1.798 | 49.98 | 7312 | 7304 | 8008 | 22624 | 38 | - - - | - - - | - - - | 7350 | 7304 | 8008 | 22624 | 2544 | 2536 | 2689 | 8154 | -193 | - - - | - - - | - - - | 2737 | 2536 | 2689 | 8154 | 8042 | 7735 | 8471 | 24247 | -0.697 | -1 | # # # | # # # | 0.961 | 0.966 | 0.863 | 0.933 | # # # | # # # | # # # | # # # | 0.997 | 0.998 | 0.915 | 0.97 | # # # | 1.341 | 1.66 | 1.53 | 1.42 | 1.46 | 1.39 | 1.41 | 33.66 | 20.01 | 29.71 | 162.09
2026-06-18 16:45 | 245.23 | 245.89 | 244.41 | 424.42 | 424.1 | 425.4 | 2.1449 | 0 | 2.3065 | 0.0003 | 1.426 | 1.428 | 1.419 | 2.031 | # # # | 1.964 | 49.99 | -103 | 0 | 404 | 301 | 103 | 0 | - - - | - - - | - - - | 0 | 404 | 301 | 516 | - - - | 393 | 909 | -516 | - - - | - - - | - - - | - - - | - - - | 393 | 909 | 526 | 0 | 564 | 1090 | -0.195 | # # # | # # # | # # # | # # # | # # # | 0.717 | 0.276 | # # # | # # # | # # # | # # # | # # # | # # # | 0.776 | 0.776 | # # # | 3.016 | 1.26 | 1.19 | 1.23 | 1.08 | 1.11 | 1.09 | 35.85 | # # # | 33.44 | 0
2026-06-18 16:55 | 243.99 | 245.18 | 243.62 | 422.74 | 422.65 | 423.79 | 2.0901 | 0 | 2.2525 | 0.0003 | 1.44 | 1.442 | 1.427 | 2.026 | # # # | 1.955 | 50 | -102 | 0 | 394 | 292 | 102 | 0 | - - - | - - - | - - - | 0 | 394 | 292 | 500 | - - - | 382 | 881 | -500 | - - - | - - - | - - - | - - - | - - - | 382 | 881 | 510 | 0 | 549 | 1059 | -0.2 | # # # | # # # | # # # | # # # | # # # | 0.718 | 0.276 | # # # | # # # | # # # | # # # | # # # | # # # | 0.786 | 0.786 | # # # | 3.019 | 1.62 | 1.66 | 1.33 | 1.54 | 1.47 | 1.29 | 35.68 | # # # | 32.52 | 0
2026-06-18 17:05 | 243.06 | 244.68 | 243.01 | 421.52 | 421.6 | 422.52 | 2.0188 | 0 | 2.3432 | 0.244 | 1.44 | 1.445 | 1.428 | 2.034 | # # # | 1.909 | 50 | -109 | 0 | 420 | 312 | 109 | 0 | - - - | - - - | - - - | 0 | 420 | 312 | 478 | - - - | 383 | 861 | -478 | - - - | - - - | - - - | - - - | - - - | 383 | 861 | 490 | 0 | 569 | 1059 | -0.222 | # # # | # # # | # # # | # # # | # # # | 0.739 | 0.295 | # # # | # # # | # # # | # # # | # # # | # # # | 0.807 | 0.807 | # # # | 2.774 | 1.43 | 1.49 | 1.22 | 1.34 | 1.31 | 1.14 | 36.78 | # # # | 30.15 | 0.99
2026-06-18 17:15 | 243.54 | 244.97 | 243.44 | 422.17 | 422.27 | 423.29 | 1.966 | 0 | 2.4844 | 1.0391 | 1.438 | 1.441 | 1.429 | 2.068 | # # # | 1.87 | 50 | -131 | 0 | 466 | 334 | 131 | 0 | - - - | - - - | - - - | 0 | 466 | 334 | 460 | - - - | 386 | 846 | -460 | - - - | - - - | - - - | - - - | - - - | 386 | 846 | 479 | 0 | 605 | 1084 | -0.275 | # # # | # # # | # # # | # # # | # # # | 0.77 | 0.308 | # # # | # # # | # # # | # # # | # # # | # # # | 0.827 | 0.827 | # # # | 2.534 | 1.29 | 1.38 | 1.22 | 1.19 | 1.23 | 1.1 | 38.23 | # # # | 29.22 | 19.47
2026-06-18 17:25 | 244.95 | 246.16 | 244.6 | 424.37 | 424.4 | 425.47 | 2.1428 | 0 | 2.3675 | 0.2668 | 1.436 | 1.439 | 1.427 | 2.054 | # # # | 1.947 | 49.97 | -116 | 0 | 421 | 305 | 116 | 0 | - - - | - - - | - - - | 0 | 421 | 305 | 512 | - - - | 397 | 908 | -512 | - - - | - - - | - - - | - - - | - - - | 397 | 908 | 525 | 0 | 579 | 1103 | -0.221 | # # # | # # # | # # # | # # # | # # # | 0.727 | 0.277 | # # # | # # # | # # # | # # # | # # # | # # # | 0.788 | 0.788 | # # # | 2.991 | 1.18 | 1.27 | 1.13 | 1.04 | 1.15 | 1 | 36.77 | # # # | 32.9 | 1.38
2026-06-18 17:35 | 245.26 | 246.37 | 244.85 | 424.82 | 424.78 | 425.96 | 2.1668 | 0 | 2.3006 | 0.0005 | 1.437 | 1.441 | 1.427 | 2.047 | # # # | 1.974 | 49.96 | -110 | 0 | 401 | 291 | 110 | 0 | - - - | - - - | - - - | 0 | 401 | 291 | 520 | - - - | 396 | 916 | -520 | - - - | - - - | - - - | - - - | - - - | 396 | 916 | 531 | 0 | 563 | 1095 | -0.207 | # # # | # # # | # # # | # # # | # # # | 0.711 | 0.266 | # # # | # # # | # # # | # # # | # # # | # # # | 0.785 | 0.785 | # # # | 3.151 | 1.31 | 1.41 | 1.2 | 1.21 | 1.27 | 1.07 | 36.73 | # # # | 34.06 | 0
2026-06-18 17:45 | 245.52 | 246.51 | 245.12 | 425.13 | 425.14 | 426.47 | 0.5322 | 0 | 0.5669 | 0.0005 | 1.439 | 1.441 | 1.429 | 0.126 | # # # | 0.121 | 50.05 | -7 | 0 | 24 | 18 | 7 | 0 | - - - | - - - | - - - | 0 | 24 | 18 | 32 | - - - | 24 | 56 | -32 | - - - | - - - | - - - | - - - | - - - | 24 | 56 | 32 | 0 | 35 | 67 | -0.952 | # # # | # # # | # # # | # # # | # # # | 0.983 | 0.269 | # # # | # # # | # # # | # # # | # # # | # # # | 0.985 | 0.985 | # # # | 0.197 | 1.25 | 1.44 | 1.17 | 1.19 | 1.26 | 1.04 | 2.49 | # # # | 2.05 | 0
2026-06-18 17:55 | 245.34 | 246.35 | 244.97 | 424.82 | 424.91 | 426.15 | 0.0207 | 0 | 0 | 0.0005 | 1.44 | 1.438 | 1.428 | 0 | # # # | # # # | 49.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.29 | 1.26 | 1.19 | 1.09 | 1.17 | 1.08 | 0 | # # # | # # # | 0
2026-06-18 18:05 | 245 | 246.16 | 244.71 | 424.42 | 424.47 | 425.62 | 0.0207 | 0 | 0 | 0.0563 | 1.441 | 1.443 | 1.429 | 0 | # # # | # # # | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.43 | 1.52 | 1.24 | 1.35 | 1.35 | 1.18 | 0 | # # # | # # # | 0.03
2026-06-18 18:15 | 245.91 | 246.64 | 245.34 | 425.64 | 425.51 | 426.86 | 0.0207 | 0 | 0 | 0.0005 | 1.427 | 1.431 | 1.424 | 0 | # # # | # # # | 49.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.29 | 1.26 | 1.19 | 1.11 | 1.12 | 1.09 | 0 | # # # | # # # | 0
2026-06-18 18:25 | 245.8 | 246.47 | 245.24 | 425.39 | 425.28 | 426.67 | 0.0207 | 0 | 0 | 0.0005 | 1.425 | 1.43 | 1.423 | 0 | # # # | # # # | 49.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.14 | 1.12 | 1.09 | 0.96 | 0.99 | 0.97 | 0 | # # # | # # # | 0
2026-06-18 18:35 | 245.89 | 246.44 | 245.19 | 425.39 | 425.23 | 426.74 | 0.0207 | 0 | 0 | 0.0005 | 1.425 | 1.431 | 1.424 | 0 | # # # | # # # | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.06 | 1.05 | 1.01 | 0.88 | 0.89 | 0.88 | 0 | # # # | # # # | 0
2026-06-18 18:45 | 245.69 | 246.11 | 244.91 | 424.88 | 424.76 | 426.35 | 0.0207 | 0 | 0 | 0.0005 | 1.426 | 1.431 | 1.423 | 0 | # # # | # # # | 49.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.04 | 1.01 | 0.98 | 0.84 | 0.85 | 0.83 | 0 | # # # | # # # | 0
2026-06-18 18:55 | 245.03 | 245.41 | 244.24 | 423.7 | 423.56 | 425.19 | 0.0207 | 0 | 0 | 0.0005 | 1.427 | 1.431 | 1.425 | 0 | # # # | # # # | 49.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 0.98 | 0.96 | 0.95 | 0.78 | 0.77 | 0.78 | 0 | # # # | # # # | 0
2026-06-18 19:05 | 244.82 | 245.2 | 244.02 | 423.31 | 423.18 | 424.85 | 0.0207 | 0 | 0 | 0.0005 | 1.425 | 1.43 | 1.423 | 0 | # # # | # # # | 49.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1 | 0.94 | 0.92 | 0.79 | 0.77 | 0.78 | 0 | # # # | # # # | 0
2026-06-18 19:15 | 244.58 | 245.07 | 243.81 | 422.95 | 422.87 | 424.51 | 1.346 | 0.1343 | 1.4249 | 0.0005 | 1.426 | 1.431 | 1.421 | 0.779 | 0.002 | 0.753 | 49.94 | -36 | 0 | 155 | 119 | 36 | 0 | - - - | - - - | - - - | 0 | 155 | 119 | 195 | - - - | 149 | 348 | -195 | - - - | - - - | - - - | - - - | - - - | 149 | 348 | 204 | 1 | 215 | 421 | -0.686 | # # # | # # # | # # # | 0.997 | 1 | 0.893 | 0.283 | # # # | # # # | # # # | # # # | 0.996 | 1 | 0.919 | 0.971 | # # # | 1.151 | 1.05 | 1.03 | 0.98 | 0.88 | 0.87 | 0.88 | 14.13 | 0.11 | 12.47 | 0
2026-06-18 19:25 | 243.38 | 244.45 | 243.01 | 421.41 | 421.56 | 422.85 | 2.0384 | 0 | 2.3799 | 0.2129 | 1.431 | 1.437 | 1.423 | 2.023 | # # # | 1.891 | 49.95 | -113 | 0 | 435 | 323 | 113 | 0 | - - - | - - - | - - - | 0 | 435 | 323 | 483 | - - - | 380 | 863 | -483 | - - - | - - - | - - - | - - - | - - - | 380 | 863 | 496 | 0 | 578 | 1074 | -0.228 | # # # | # # # | # # # | # # # | # # # | 0.752 | 0.301 | # # # | # # # | # # # | # # # | # # # | # # # | 0.809 | 0.809 | # # # | 2.686 | 1.42 | 1.33 | 1.2 | 1.26 | 1.16 | 1.16 | 35.23 | # # # | 30.49 | 0.98
2026-06-18 19:35 | 242.08 | 243.86 | 242.23 | 419.76 | 420.2 | 421.19 | 1.9544 | 0 | 2.4292 | 0.7478 | 1.44 | 1.446 | 1.429 | 2.023 | # # # | 1.845 | 49.96 | -124 | 0 | 456 | 332 | 124 | 0 | - - - | - - - | - - - | 0 | 456 | 332 | 457 | - - - | 372 | 829 | -457 | - - - | - - - | - - - | - - - | - - - | 372 | 829 | 473 | 0 | 588 | 1061 | -0.261 | # # # | # # # | # # # | # # # | # # # | 0.774 | 0.313 | # # # | # # # | # # # | # # # | # # # | # # # | 0.837 | 0.837 | # # # | 2.497 | 1.56 | 1.64 | 1.31 | 1.47 | 1.44 | 1.31 | 34.99 | # # # | 28.61 | 11.87
2026-06-18 19:45 | 242.46 | 244.14 | 242.57 | 420.31 | 420.78 | 421.81 | 1.9617 | 0 | 2.4332 | 1.2288 | 1.437 | 1.443 | 1.43 | 2.022 | # # # | 1.829 | 49.99 | -142 | 0 | 472 | 329 | 142 | 0 | - - - | - - - | - - - | 0 | 472 | 329 | 453 | - - - | 354 | 808 | -453 | - - - | - - - | - - - | - - - | - - - | 354 | 808 | 475 | 0 | 590 | 1066 | -0.299 | # # # | # # # | # # # | # # # | # # # | 0.799 | 0.309 | # # # | # # # | # # # | # # # | # # # | # # # | 0.864 | 0.864 | # # # | 2.454 | 1.54 | 1.53 | 1.39 | 1.38 | 1.38 | 1.35 | 35.64 | # # # | 29.02 | 18.32
2026-06-18 19:55 | 241.71 | 243.84 | 242.08 | 419.37 | 420.02 | 420.83 | 2.044 | 0 | 2.3826 | 1.3347 | 1.437 | 1.441 | 1.429 | 1.98 | # # # | 1.829 | 49.97 | -157 | 0 | 475 | 318 | 157 | 0 | - - - | - - - | - - - | 0 | 475 | 318 | 468 | - - - | 328 | 796 | -468 | - - - | - - - | - - - | - - - | - - - | 328 | 796 | 494 | 0 | 577 | 1071 | -0.317 | # # # | # # # | # # # | # # # | # # # | 0.823 | 0.297 | # # # | # # # | # # # | # # # | # # # | # # # | 0.883 | 0.883 | # # # | 2.506 | 1.75 | 1.55 | 1.4 | 1.52 | 1.39 | 1.44 | 32.37 | # # # | 30.14 | 24.25
2026-06-18 20:05 | 242.53 | 244.09 | 242.53 | 420.37 | 420.69 | 421.82 | 1.9356 | 0 | 2.452 | 1.0489 | 1.437 | 1.445 | 1.43 | 2.041 | # # # | 1.843 | 49.97 | -134 | 0 | 464 | 329 | 134 | 0 | - - - | - - - | - - - | 0 | 464 | 329 | 450 | - - - | 372 | 822 | -450 | - - - | - - - | - - - | - - - | - - - | 372 | 822 | 469 | 0 | 595 | 1064 | -0.286 | # # # | # # # | # # # | # # # | # # # | 0.78 | 0.309 | # # # | # # # | # # # | # # # | # # # | # # # | 0.842 | 0.842 | # # # | 2.496 | 1.55 | 1.67 | 1.4 | 1.48 | 1.5 | 1.36 | 35.76 | # # # | 28.92 | 16.03
2026-06-18 20:15 | 243.19 | 244.51 | 243 | 421.26 | 421.52 | 422.76 | 1.5461 | 0 | 1.9263 | 0.1993 | 1.437 | 1.445 | 1.43 | 1.251 | # # # | 1.142 | 49.97 | -73 | 0 | 277 | 204 | 73 | 0 | - - - | - - - | - - - | 0 | 277 | 204 | 285 | - - - | 240 | 525 | -285 | - - - | - - - | - - - | - - - | - - - | 240 | 525 | 294 | 0 | 367 | 661 | -0.54 | # # # | # # # | # # # | # # # | # # # | 0.851 | 0.309 | # # # | # # # | # # # | # # # | # # # | # # # | 0.889 | 0.889 | # # # | 1.584 | 1.51 | 1.57 | 1.33 | 1.37 | 1.43 | 1.29 | 22.87 | # # # | 17.54 | 0.84
2026-06-18 20:25 | 242.17 | 244.11 | 242.35 | 419.99 | 420.49 | 421.48 | 0.0207 | 0 | 0 | 0.8119 | 1.439 | 1.446 | 1.431 | 0 | # # # | # # # | 49.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.55 | 1.58 | 1.34 | 1.42 | 1.4 | 1.32 | 0 | # # # | # # # | 8.66
2026-06-18 20:35 | 241.97 | 243.98 | 242.19 | 419.69 | 420.26 | 421.17 | 0.0207 | 0 | 0 | 1.5987 | 1.436 | 1.443 | 1.429 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.63 | 1.48 | 1.31 | 1.42 | 1.29 | 1.32 | 0 | # # # | # # # | 21.41
2026-06-18 20:45 | 242.69 | 244.46 | 242.7 | 420.75 | 421.09 | 422.23 | 0.0207 | 0 | 0 | 0.5119 | 1.438 | 1.447 | 1.428 | 0 | # # # | # # # | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.57 | 1.64 | 1.35 | 1.49 | 1.46 | 1.31 | 0 | # # # | # # # | 4.06
2026-06-18 20:55 | 242.53 | 244.29 | 242.59 | 420.4 | 420.9 | 422.03 | 0.0207 | 0 | 0 | 1.4367 | 1.435 | 1.441 | 1.428 | 0 | # # # | # # # | 49.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.52 | 1.5 | 1.3 | 1.37 | 1.31 | 1.31 | 0 | # # # | # # # | 19.94
2026-06-18 21:05 | 242.06 | 244.16 | 242.34 | 419.91 | 420.49 | 421.44 | 0.0207 | 0 | 0 | 1.1063 | 1.435 | 1.442 | 1.427 | 0 | # # # | # # # | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.6 | 1.52 | 1.34 | 1.43 | 1.35 | 1.31 | 0 | # # # | # # # | 16.82
2026-06-18 21:15 | 243.75 | 245.05 | 243.47 | 422.2 | 422.4 | 423.69 | 0.0207 | 0 | 0 | 0.4425 | 1.438 | 1.445 | 1.426 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.54 | 1.65 | 1.27 | 1.5 | 1.41 | 1.24 | 0 | # # # | # # # | 2.18
2026-06-18 21:25 | 241.72 | 244.14 | 242.29 | 419.66 | 420.3 | 421.18 | 0.0207 | 0 | 0 | 1.6084 | 1.434 | 1.44 | 1.425 | 0 | # # # | # # # | 49.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.68 | 1.58 | 1.34 | 1.53 | 1.36 | 1.34 | 0 | # # # | # # # | 18.06
2026-06-18 21:35 | 243.72 | 245.27 | 243.64 | 422.38 | 422.63 | 423.9 | 0.0207 | 0 | 0 | 1.0913 | 1.438 | 1.444 | 1.426 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.66 | 1.71 | 1.35 | 1.59 | 1.49 | 1.35 | 0 | # # # | # # # | 14.41
2026-06-18 21:45 | 243.81 | 245.43 | 243.72 | 422.53 | 422.88 | 424.06 | 0.0207 | 0 | 0 | 1.268 | 1.435 | 1.44 | 1.424 | 0 | # # # | # # # | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.65 | 1.57 | 1.33 | 1.5 | 1.36 | 1.34 | 0 | # # # | # # # | 21.22
2026-06-18 21:55 | 242.53 | 244.52 | 242.75 | 420.69 | 421.12 | 422.16 | 0.0207 | 0 | 0 | 1.1452 | 1.434 | 1.444 | 1.423 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.02 | 2 | 1.49 | 1.99 | 1.69 | 1.55 | 0 | # # # | # # # | 17.34
2026-06-18 22:05 | 243.1 | 244.59 | 243.03 | 421.29 | 421.49 | 422.79 | 0.0207 | 0 | 0 | 1.0582 | 1.438 | 1.449 | 1.425 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.9 | 2.08 | 1.47 | 1.97 | 1.78 | 1.45 | 0 | # # # | # # # | 13.61
2026-06-18 22:15 | 242.87 | 244.57 | 242.89 | 421.07 | 421.33 | 422.51 | 0.0207 | 0 | 0 | 0.1886 | 1.438 | 1.451 | 1.426 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.21 | 2.52 | 1.75 | 2.35 | 2.22 | 1.7 | 0 | # # # | # # # | 0.65
2026-06-18 22:25 | 242.87 | 244.76 | 243.01 | 421.18 | 421.64 | 422.62 | 0.0207 | 0 | 0 | 1.4875 | 1.435 | 1.448 | 1.424 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.23 | 2.44 | 1.83 | 2.3 | 2.18 | 1.78 | 0 | # # # | # # # | 17.68
2026-06-18 22:35 | 243.97 | 245.58 | 243.83 | 422.85 | 423.09 | 424.24 | 0.0207 | 0 | 0 | 0.9965 | 1.44 | 1.452 | 1.428 | 0 | # # # | # # # | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.29 | 2.5 | 1.81 | 2.34 | 2.25 | 1.78 | 0 | # # # | # # # | 9.38
2026-06-18 22:45 | 243.34 | 245.22 | 243.49 | 422.07 | 422.4 | 423.42 | 0.0207 | 0 | 0 | 1.0475 | 1.442 | 1.457 | 1.433 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.17 | 2.71 | 1.81 | 2.42 | 2.39 | 1.65 | 0 | # # # | # # # | 14.12
2026-06-18 22:55 | 243.94 | 245.79 | 243.97 | 422.95 | 423.4 | 424.38 | 0.0207 | 0 | 0 | 1.2587 | 1.44 | 1.45 | 1.429 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.05 | 2.09 | 1.67 | 1.99 | 1.91 | 1.62 | 0 | # # # | # # # | 20.38
2026-06-18 23:05 | 244.16 | 245.73 | 244.02 | 423.13 | 423.44 | 424.54 | 0.0207 | 0 | 0 | 1.2162 | 1.443 | 1.458 | 1.433 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.05 | 2.45 | 1.7 | 2.22 | 2.15 | 1.58 | 0 | # # # | # # # | 20.94
2026-06-18 23:15 | 244.02 | 245.75 | 243.95 | 423.02 | 423.32 | 424.43 | 0.0207 | 0 | 0 | 0.878 | 1.443 | 1.458 | 1.43 | 0 | # # # | # # # | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.22 | 2.5 | 1.78 | 2.33 | 2.23 | 1.71 | 0 | # # # | # # # | 9.63
2026-06-18 23:25 | 243.46 | 245.54 | 243.64 | 422.29 | 422.86 | 423.73 | 0.0207 | 0 | 0 | 1.3348 | 1.443 | 1.452 | 1.43 | 0 | # # # | # # # | 49.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.33 | 2.36 | 1.72 | 2.32 | 2.07 | 1.75 | 0 | # # # | # # # | 22.48
2026-06-18 23:35 | 243.52 | 245.01 | 243.28 | 421.96 | 422.16 | 423.35 | 0.0207 | 0 | 0 | 0.3358 | 1.446 | 1.457 | 1.433 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.32 | 2.56 | 1.88 | 2.4 | 2.31 | 1.86 | 0 | # # # | # # # | 1.87
2026-06-18 23:45 | 240.26 | 242.26 | 240.35 | 416.72 | 417.15 | 418.12 | 0.0207 | 0 | 0 | 1.2593 | 1.438 | 1.449 | 1.424 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.43 | 2.36 | 1.83 | 2.38 | 2.1 | 1.9 | 0 | # # # | # # # | 14.14
2026-06-18 23:55 | 241.5 | 243.12 | 241.27 | 418.59 | 418.75 | 419.88 | 0.0207 | 0 | 0 | 0.1107 | 1.449 | 1.459 | 1.427 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 3.49 | 3.52 | 2.26 | 3.69 | 2.93 | 2.49 | 0 | # # # | # # # | 0.38
2026-06-19 00:05 | 244.03 | 244.49 | 243.02 | 421.96 | 421.67 | 423.38 | 0.0207 | 0 | 0 | 0.0003 | 1.422 | 1.429 | 1.42 | 0 | # # # | # # # | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.31 | 1.23 | 1.33 | 1.14 | 1.16 | 1.22 | 0 | # # # | # # # | 0
2026-06-19 00:15 | 243.86 | 244.33 | 242.87 | 421.68 | 421.39 | 423.11 | 0.0207 | 0 | 0 | 0.0003 | 1.422 | 1.428 | 1.42 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.26 | 1.17 | 1.26 | 1.07 | 1.1 | 1.13 | 0 | # # # | # # # | 0
2026-06-19 00:25 | 242.24 | 242.69 | 241.23 | 418.87 | 418.56 | 420.27 | 0.0207 | 0 | 0 | 0.0003 | 1.423 | 1.432 | 1.422 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.35 | 1.32 | 1.36 | 1.2 | 1.23 | 1.25 | 0 | # # # | # # # | 0
2026-06-19 00:35 | 241.32 | 241.73 | 240.32 | 417.28 | 416.95 | 418.65 | 0.0207 | 0 | 0 | 0.0003 | 1.423 | 1.432 | 1.422 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.38 | 1.33 | 1.43 | 1.24 | 1.27 | 1.3 | 0 | # # # | # # # | 0
2026-06-19 00:45 | 241.26 | 241.69 | 240.25 | 417.18 | 416.83 | 418.55 | 0.0207 | 0 | 0 | 0.0003 | 1.424 | 1.433 | 1.423 | 0 | # # # | # # # | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.42 | 1.31 | 1.41 | 1.22 | 1.26 | 1.3 | 0 | # # # | # # # | 0
2026-06-19 00:55 | 241.23 | 241.63 | 240.25 | 417.13 | 416.79 | 418.5 | 0.0207 | 0 | 0 | 0.0003 | 1.424 | 1.433 | 1.424 | 0 | # # # | # # # | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.38 | 1.33 | 1.4 | 1.22 | 1.26 | 1.31 | 0 | # # # | # # # | 0
2026-06-19 01:05 | 241.41 | 241.82 | 240.41 | 417.44 | 417.09 | 418.81 | 0.0207 | 0 | 0 | 0.0003 | 1.423 | 1.432 | 1.421 | 0 | # # # | # # # | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.33 | 1.28 | 1.39 | 1.17 | 1.22 | 1.26 | 0 | # # # | # # # | 0
2026-06-19 01:15 | 239.74 | 241 | 239.29 | 415.19 | 415.32 | 416.56 | 0.0207 | 0 | 0 | 1.2564 | 1.429 | 1.437 | 1.43 | 0 | # # # | # # # | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.8 | 1.66 | 1.53 | 1.62 | 1.5 | 1.54 | 0 | # # # | # # # | 13.07
2026-06-19 01:25 | 238.66 | 240.52 | 238.32 | 413.8 | 413.96 | 414.93 | 0.0207 | 0 | 0 | 1.0047 | 1.446 | 1.459 | 1.43 | 0 | # # # | # # # | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 3.03 | 3.15 | 2.1 | 3.23 | 2.64 | 2.2 | 0 | # # # | # # # | 7.28
2026-06-19 01:35 | 238.76 | 240.7 | 238.5 | 414.08 | 414.22 | 415.18 | 0.0207 | 0 | 0 | 0.568 | 1.455 | 1.474 | 1.433 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 3.43 | 3.85 | 2.37 | 3.86 | 3.26 | 2.36 | 0 | # # # | # # # | 5.56
2026-06-19 01:45 | 239.35 | 241.06 | 238.96 | 414.8 | 415.03 | 416.11 | 0.0207 | 0 | 0 | 0.8159 | 1.447 | 1.463 | 1.433 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.14 | 2.58 | 1.85 | 2.32 | 2.32 | 1.71 | 0 | # # # | # # # | 8.38
2026-06-19 01:55 | 239.06 | 241.02 | 238.85 | 414.49 | 414.84 | 415.83 | 0.0207 | 0 | 0 | 1.0918 | 1.444 | 1.457 | 1.428 | 0 | # # # | # # # | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.14 | 2.26 | 1.66 | 2.16 | 1.97 | 1.65 | 0 | # # # | # # # | 12.42
2026-06-19 02:05 | 238.7 | 240.86 | 238.68 | 414.07 | 414.5 | 415.4 | 0.0207 | 0 | 0 | 1.0905 | 1.439 | 1.451 | 1.424 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.93 | 2.06 | 1.58 | 1.93 | 1.81 | 1.53 | 0 | # # # | # # # | 11.55
2026-06-19 02:15 | 239.87 | 241.53 | 239.43 | 415.66 | 415.82 | 416.98 | 0.0207 | 0 | 0 | 0.6182 | 1.443 | 1.455 | 1.428 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.23 | 2.42 | 1.84 | 2.28 | 2.19 | 1.77 | 0 | # # # | # # # | 4.02
2026-06-19 02:25 | 238.2 | 240.59 | 238.29 | 413.38 | 413.89 | 414.68 | 0.0207 | 0 | 0 | 1.5406 | 1.442 | 1.456 | 1.428 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.23 | 2.28 | 1.74 | 2.19 | 2.01 | 1.76 | 0 | # # # | # # # | 19.69
2026-06-19 02:35 | 239.36 | 241.18 | 239.04 | 414.95 | 415.15 | 416.19 | 0.0207 | 0 | 0 | 0.3863 | 1.444 | 1.459 | 1.43 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.28 | 2.57 | 1.86 | 2.38 | 2.31 | 1.78 | 0 | # # # | # # # | 2.05
2026-06-19 02:45 | 238.75 | 240.87 | 238.66 | 414.16 | 414.51 | 415.36 | 0.0207 | 0 | 0 | 1.0749 | 1.44 | 1.452 | 1.426 | 0 | # # # | # # # | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.92 | 2.12 | 1.63 | 1.95 | 1.91 | 1.51 | 0 | # # # | # # # | 13.47
2026-06-19 02:55 | 239.16 | 241.08 | 238.9 | 414.68 | 414.94 | 415.92 | 0.0207 | 0 | 0 | 0.9599 | 1.448 | 1.461 | 1.43 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.33 | 2.56 | 1.84 | 2.4 | 2.29 | 1.79 | 0 | # # # | # # # | 10.52
2026-06-19 03:05 | 239.02 | 241.01 | 238.83 | 414.53 | 414.77 | 415.74 | 0.0207 | 0 | 0 | 0.783 | 1.453 | 1.466 | 1.435 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.61 | 2.82 | 1.94 | 2.72 | 2.48 | 1.95 | 0 | # # # | # # # | 6.5
2026-06-19 03:15 | 239.3 | 241.2 | 239.08 | 414.88 | 415.25 | 416.16 | 0.0207 | 0 | 0 | 1.2098 | 1.448 | 1.463 | 1.434 | 0 | # # # | # # # | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.35 | 2.65 | 1.77 | 2.56 | 2.27 | 1.7 | 0 | # # # | # # # | 18
2026-06-19 03:25 | 239.48 | 241.44 | 239.24 | 415.29 | 415.49 | 416.5 | 0.0207 | 0 | 0 | 0.3617 | 1.45 | 1.464 | 1.432 | 0 | # # # | # # # | 50.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.65 | 2.93 | 1.99 | 2.86 | 2.56 | 1.95 | 0 | # # # | # # # | 2.06
2026-06-19 03:35 | 240.17 | 241.75 | 239.67 | 416.13 | 416.25 | 417.39 | 0.0207 | 0 | 0 | 0.8178 | 1.446 | 1.458 | 1.429 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.41 | 2.55 | 1.86 | 2.45 | 2.28 | 1.86 | 0 | # # # | # # # | 10.39
2026-06-19 03:45 | 240.1 | 241.86 | 239.76 | 416.13 | 416.4 | 417.45 | 0.0207 | 0 | 0 | 0.961 | 1.451 | 1.461 | 1.433 | 0 | # # # | # # # | 50.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.51 | 2.59 | 1.9 | 2.52 | 2.31 | 1.93 | 0 | # # # | # # # | 14.43
2026-06-19 03:55 | 239.53 | 241.73 | 239.55 | 415.61 | 415.97 | 416.83 | 0.0207 | 0 | 0 | 1.1643 | 1.442 | 1.455 | 1.427 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.22 | 2.35 | 1.71 | 2.27 | 2.05 | 1.71 | 0 | # # # | # # # | 16.15
2026-06-19 04:05 | 240.76 | 242.5 | 240.41 | 417.29 | 417.51 | 418.57 | 0.0207 | 0 | 0 | 0.7451 | 1.444 | 1.454 | 1.427 | 0 | # # # | # # # | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.08 | 2.14 | 1.62 | 2.06 | 1.87 | 1.65 | 0 | # # # | # # # | 8.78
2026-06-19 04:15 | 240.02 | 242.06 | 239.87 | 416.29 | 416.57 | 417.51 | 0.0207 | 0 | 0 | 1.2753 | 1.446 | 1.456 | 1.427 | 0 | # # # | # # # | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.22 | 2.22 | 1.67 | 2.22 | 1.95 | 1.68 | 0 | # # # | # # # | 21.39
2026-06-19 04:25 | 240.84 | 242.56 | 240.42 | 417.43 | 417.52 | 418.67 | 0.0207 | 0 | 0 | 0.5855 | 1.448 | 1.458 | 1.43 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.19 | 2.34 | 1.72 | 2.23 | 2.06 | 1.71 | 0 | # # # | # # # | 4.96
2026-06-19 04:35 | 240.86 | 242.59 | 240.45 | 417.43 | 417.67 | 418.68 | 0.0207 | 0 | 0 | 1.1711 | 1.446 | 1.454 | 1.43 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.98 | 1.98 | 1.55 | 1.92 | 1.74 | 1.54 | 0 | # # # | # # # | 25.11
2026-06-19 04:45 | 240.52 | 242.17 | 239.99 | 416.82 | 416.89 | 417.95 | 0.0207 | 0 | 0 | 0.1514 | 1.449 | 1.459 | 1.434 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.23 | 2.38 | 1.77 | 2.27 | 2.14 | 1.73 | 0 | # # # | # # # | 0.54
2026-06-19 04:55 | 240.45 | 242.25 | 239.95 | 416.77 | 416.87 | 417.95 | 0.0207 | 0 | 0 | 0.4604 | 1.449 | 1.459 | 1.435 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.68 | 2.56 | 2.09 | 2.57 | 2.36 | 2.18 | 0 | # # # | # # # | 3.21
2026-06-19 05:05 | 241.17 | 242.41 | 240.35 | 417.55 | 417.51 | 418.77 | 0.0207 | 0 | 0 | 0.7437 | 1.423 | 1.434 | 1.422 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 2.02 | 1.62 | 1.77 | 1.71 | 1.57 | 1.86 | 0 | # # # | # # # | 8.39
2026-06-19 05:15 | 242.11 | 242.97 | 240.95 | 418.84 | 418.57 | 420.04 | 0.0207 | 0 | 0 | 0 | 1.422 | 1.433 | 1.421 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.68 | 1.41 | 1.52 | 1.42 | 1.34 | 1.52 | 0 | # # # | # # # | # # #
2026-06-19 05:25 | 242.4 | 243.2 | 241.25 | 419.33 | 418.99 | 420.57 | 0.0207 | 0 | 0 | 0 | 1.422 | 1.432 | 1.421 | 0 | # # # | # # # | 50.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.26 | 1.13 | 1.25 | 1.05 | 1.05 | 1.12 | 0 | # # # | # # # | # # #
2026-06-19 05:35 | 242.61 | 243.37 | 241.44 | 419.68 | 419.33 | 420.87 | 0.0207 | 0 | 0 | 0 | 1.424 | 1.432 | 1.421 | 0 | # # # | # # # | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.3 | 1.14 | 1.25 | 1.09 | 1.05 | 1.14 | 0 | # # # | # # # | # # #
2026-06-19 05:45 | 242.56 | 243.29 | 241.37 | 419.55 | 419.23 | 420.75 | 0.0207 | 0 | 0 | 0 | 1.423 | 1.431 | 1.421 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.27 | 1.13 | 1.22 | 1.06 | 1.03 | 1.12 | 0 | # # # | # # # | # # #
2026-06-19 05:55 | 242.68 | 243.34 | 241.47 | 419.66 | 419.36 | 420.98 | 0.0207 | 0 | 0 | 0 | 1.424 | 1.432 | 1.421 | 0 | # # # | # # # | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.26 | 1.17 | 1.24 | 1.07 | 1.05 | 1.13 | 0 | # # # | # # # | # # #
2026-06-19 06:05 | 242.82 | 243.49 | 241.63 | 419.91 | 419.63 | 421.24 | 0.0207 | 0 | 0 | 0 | 1.422 | 1.433 | 1.421 | 0 | # # # | # # # | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.2 | 1.12 | 1.19 | 1.01 | 1 | 1.04 | 0 | # # # | # # # | # # #
2026-06-19 06:15 | 242.86 | 243.38 | 241.51 | 419.84 | 419.46 | 421.15 | 0.0207 | 0 | 0 | 0 | 1.423 | 1.432 | 1.422 | 0 | # # # | # # # | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.29 | 1.18 | 1.23 | 1.11 | 1.08 | 1.12 | 0 | # # # | # # # | # # #
2026-06-19 06:25 | 243.04 | 243.49 | 241.61 | 420.09 | 419.68 | 421.36 | 0.0207 | 0 | 0 | 0 | 1.424 | 1.433 | 1.422 | 0 | # # # | # # # | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.29 | 1.19 | 1.25 | 1.12 | 1.08 | 1.13 | 0 | # # # | # # # | # # #
2026-06-19 06:35 | 243.29 | 243.74 | 241.94 | 420.55 | 420.18 | 421.84 | 0.0207 | 0 | 0 | 0 | 1.427 | 1.431 | 1.424 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.36 | 1.25 | 1.33 | 1.19 | 1.17 | 1.19 | 0 | # # # | # # # | # # #
2026-06-19 06:45 | 243.45 | 243.97 | 242.05 | 420.88 | 420.47 | 422.07 | 0.0207 | 0 | 0 | 0 | 1.426 | 1.43 | 1.423 | 0 | # # # | # # # | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.31 | 1.2 | 1.26 | 1.13 | 1.09 | 1.12 | 0 | # # # | # # # | # # #
2026-06-19 06:55 | 243.65 | 244.19 | 242.24 | 421.24 | 420.79 | 422.45 | 0.0207 | 0 | 0 | 0 | 1.426 | 1.43 | 1.424 | 0 | # # # | # # # | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.27 | 1.18 | 1.24 | 1.09 | 1.06 | 1.08 | 0 | # # # | # # # | # # #
2026-06-19 07:05 | 243.21 | 243.93 | 242 | 420.65 | 420.32 | 421.88 | 0.0207 | 0 | 0 | 0 | 1.426 | 1.431 | 1.424 | 0 | # # # | # # # | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.25 | 1.16 | 1.25 | 1.07 | 1.06 | 1.07 | 0 | # # # | # # # | # # #
2026-06-19 07:15 | 242.9 | 243.61 | 241.68 | 420.13 | 419.78 | 421.29 | 0.0207 | 0 | 0 | 0 | 1.427 | 1.432 | 1.425 | 0 | # # # | # # # | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.17 | 1.1 | 1.14 | 0.99 | 0.97 | 0.97 | 0 | # # # | # # # | # # #
2026-06-19 07:25 | 242.39 | 243.3 | 241.27 | 419.41 | 419.08 | 420.57 | 1.1592 | 0.1328 | 1.2952 | 0.0512 | 1.428 | 1.434 | 1.427 | 0.694 | 0.002 | 0.66 | 50.02 | -28 | 0 | 138 | 109 | 29 | 0 | - - - | - - - | 1 | 0 | 138 | 109 | -154 | - - - | 121 | 282 | -158 | - - - | - - - | - - - | 4 | - - - | 121 | 282 | 165 | 1 | 184 | 350 | -0.719 | # # # | # # # | # # # | 0.997 | 1 | 0.914 | 0.311 | # # # | # # # | # # # | # # # | 0.995 | 0.999 | 0.938 | 0.977 | # # # | 0.914 | 1.22 | 1.1 | 1.18 | 1.02 | 0.98 | 1 | 12.24 | 0.12 | 10.08 | 0.03
2026-06-19 07:35 | 239.33 | 241.61 | 239.24 | 415.36 | 415.63 | 416.34 | 1.8264 | 0 | 2.2737 | 1.2011 | 1.432 | 1.443 | 1.423 | 1.983 | # # # | 1.796 | 49.99 | -123 | 0 | 447 | 325 | 123 | 0 | - - - | - - - | - - - | 0 | 447 | 325 | 419 | - - - | 308 | 727 | -419 | - - - | - - - | - - - | - - - | - - - | 308 | 727 | 437 | 0 | 544 | 981 | -0.281 | # # # | # # # | # # # | # # # | # # # | 0.823 | 0.331 | # # # | # # # | # # # | # # # | # # # | # # # | 0.883 | 0.883 | # # # | 2.24 | 1.75 | 1.64 | 1.37 | 1.63 | 1.38 | 1.38 | 33.68 | # # # | 27.39 | 15.66
2026-06-19 07:45 | 238.72 | 241.06 | 238.72 | 414.27 | 414.72 | 415.43 | 32.4365 | 31.7378 | 34.7823 | 1.2479 | 1.435 | 1.445 | 1.427 | 1.833 | 1.123 | 1.753 | 49.97 | 5703 | 5726 | 6423 | 17852 | 38 | - - - | - - - | - - - | 5741 | 5726 | 6423 | 17852 | 2104 | 2088 | 2207 | 6716 | -158 | - - - | - - - | - - - | 2262 | 2088 | 2207 | 6716 | 6337 | 6099 | 6802 | 19238 | -0.724 | # # # | # # # | # # # | 0.956 | 0.963 | 0.901 | 0.928 | # # # | # # # | # # # | # # # | 0.992 | 0.999 | 0.952 | 0.981 | # # # | 1.095 | 1.54 | 1.42 | 1.31 | 1.36 | 1.2 | 1.27 | 32.27 | 19.14 | 28.17 | 135.48
2026-06-19 07:55 | 237.04 | 239.73 | 237.42 | 411.77 | 412.27 | 412.9 | 26.0209 | 25.4929 | 27.9405 | 1.3326 | 1.434 | 1.446 | 1.426 | 1.932 | 0.75 | 1.775 | 50.03 | 3584 | 3662 | 4257 | 11503 | 65 | - - - | - - - | - - - | 3649 | 3662 | 4257 | 11503 | 1221 | 1369 | 1554 | 4620 | -238 | - - - | - - - | - - - | 1459 | 1369 | 1554 | 4620 | 4181 | 3913 | 4546 | 12640 | -0.565 | # # # | # # # | # # # | 0.971 | 0.975 | 0.872 | 0.91 | # # # | # # # | # # # | # # # | 0.996 | 0.998 | 0.929 | 0.974 | # # # | 1.449 | 1.6 | 1.53 | 1.34 | 1.48 | 1.3 | 1.29 | 32.67 | 13.49 | 27.28 | 89.65
2026-06-19 08:05 | 237.78 | 240.29 | 237.93 | 412.81 | 413.35 | 413.9 | 35.2262 | 34.7242 | 37.6297 | 1.3184 | 1.434 | 1.446 | 1.43 | 1.777 | 1.125 | 1.701 | 50.04 | 6354 | 6418 | 7077 | 19849 | 33 | - - - | - - - | - - - | 6387 | 6418 | 7077 | 19849 | 2259 | 2233 | 2332 | 7106 | -141 | - - - | - - - | - - - | 2400 | 2233 | 2332 | 7106 | 6971 | 6797 | 7460 | 21229 | -0.742 | # # # | # # # | # # # | 0.956 | 0.962 | 0.906 | 0.935 | # # # | # # # | # # # | # # # | 0.993 | 1 | 0.955 | 0.983 | # # # | 1.013 | 1.79 | 1.57 | 1.38 | 1.53 | 1.35 | 1.48 | 30.72 | 20.31 | 28.31 | 190.27
2026-06-19 08:15 | 241.63 | 243.51 | 241.36 | 418.93 | 419.24 | 420.11 | 27.2739 | 26.6693 | 29.2073 | 1.3624 | 1.438 | 1.445 | 1.43 | 1.908 | 0.717 | 1.769 | 49.98 | 3862 | 3924 | 4564 | 12349 | 80 | - - - | - - - | - - - | 3942 | 3924 | 4564 | 12349 | 1251 | 1395 | 1605 | 4767 | -258 | - - - | - - - | - - - | 1509 | 1395 | 1605 | 4767 | 4494 | 4167 | 4856 | 13517 | -0.586 | # # # | # # # | # # # | 0.973 | 0.976 | 0.866 | 0.914 | # # # | # # # | # # # | # # # | 0.994 | 1 | 0.923 | 0.972 | # # # | 1.532 | 1.42 | 1.37 | 1.28 | 1.23 | 1.19 | 1.22 | 32.73 | 13.06 | 28.84 | 109.56
2026-06-19 08:25 | 241.08 | 243.39 | 241.13 | 418.36 | 418.81 | 419.55 | 1.9381 | 0.0067 | 2.3085 | 0.9994 | 1.437 | 1.444 | 1.429 | 1.988 | 0 | 1.821 | 50.04 | -133 | 0 | 452 | 319 | 133 | 0 | - - - | - - - | - - - | 0 | 452 | 319 | 447 | - - - | 324 | 771 | -447 | - - - | - - - | - - - | - - - | - - - | 324 | 771 | 467 | 0 | 556 | 1024 | -0.285 | # # # | # # # | # # # | # # # | # # # | 0.813 | 0.312 | # # # | # # # | # # # | # # # | # # # | # # # | 0.88 | 0.88 | # # # | 2.416 | 1.42 | 1.32 | 1.22 | 1.18 | 1.13 | 1.17 | 33.56 | 0 | 28.71 | 9.78
2026-06-19 08:35 | 241.79 | 243.72 | 241.56 | 419.17 | 419.6 | 420.49 | 39.0755 | 38.4698 | 41.937 | 1.6206 | 1.438 | 1.444 | 1.433 | 1.763 | 1.43 | 1.682 | 50.05 | 8099 | 8136 | 8935 | 25170 | 20 | - - - | - - - | - - - | 8119 | 8136 | 8935 | 25170 | 2978 | 2810 | 2870 | 8792 | -67 | - - - | - - - | - - - | 3045 | 2810 | 2870 | 8792 | 8742 | 8608 | 9391 | 26741 | -0.889 | # # # | # # # | # # # | 0.946 | 0.953 | 0.929 | 0.941 | # # # | # # # | # # # | # # # | 0.993 | 0.999 | 0.974 | 0.989 | # # # | 0.656 | 1.47 | 1.37 | 1.32 | 1.22 | 1.2 | 1.26 | 31.21 | 26.78 | 28.4 | 260.51
2026-06-19 08:45 | 241.75 | 243.77 | 241.5 | 419.2 | 419.53 | 420.42 | 20.5354 | 20.2551 | 22.034 | 1.1433 | 1.436 | 1.444 | 1.431 | 1.939 | 0.413 | 1.805 | 50.04 | 2114 | 2241 | 2774 | 7130 | 106 | - - - | - - - | - - - | 2220 | 2241 | 2774 | 7130 | 512 | 760 | 1059 | 3043 | -355 | - - - | - - - | - - - | 867 | 760 | 1059 | 3043 | 2755 | 2384 | 2988 | 8127 | -0.451 | -1 | # # # | # # # | 0.984 | 0.986 | 0.842 | 0.877 | # # # | # # # | # # # | # # # | 0.997 | 1 | 0.902 | 0.966 | # # # | 2.008 | 1.69 | 1.48 | 1.37 | 1.42 | 1.31 | 1.4 | 32.27 | 7.53 | 29.81 | 76.59
2026-06-19 08:55 | 241.46 | 243.63 | 241.34 | 418.82 | 419.25 | 420.07 | 37.2968 | 36.758 | 40.0911 | 1.5839 | 1.44 | 1.446 | 1.433 | 1.787 | 1.306 | 1.697 | 50.04 | 7362 | 7422 | 8191 | 22975 | 29 | - - - | - - - | - - - | 7391 | 7422 | 8191 | 22975 | 2683 | 2577 | 2662 | 8120 | -99 | - - - | - - - | - - - | 2782 | 2577 | 2662 | 8120 | 8003 | 7858 | 8622 | 24483 | -0.837 | # # # | # # # | # # # | 0.95 | 0.957 | 0.915 | 0.938 | # # # | # # # | # # # | # # # | 0.993 | 0.998 | 0.964 | 0.985 | # # # | 0.819 | 1.67 | 1.53 | 1.45 | 1.42 | 1.37 | 1.44 | 32.39 | 23.66 | 27.88 | 152.89
2026-06-19 09:05 | 242.84 | 244.37 | 242.24 | 420.7 | 420.8 | 421.89 | 23.5618 | 23.2583 | 25.2474 | 0.934 | 1.438 | 1.446 | 1.431 | 1.938 | 0.542 | 1.85 | 50.05 | 2850 | 2950 | 3473 | 9273 | 70 | - - - | - - - | - - - | 2920 | 2950 | 3473 | 9273 | 801 | 1061 | 1313 | 3846 | -336 | - - - | - - - | - - - | 1137 | 1061 | 1313 | 3846 | 3479 | 3137 | 3743 | 10359 | -0.448 | # # # | # # # | # # # | 0.979 | 0.982 | 0.806 | 0.895 | # # # | # # # | # # # | # # # | 0.997 | 0.999 | 0.862 | 0.952 | # # # | 2.032 | 1.75 | 1.55 | 1.49 | 1.5 | 1.43 | 1.51 | 33.87 | 10.32 | 29.54 | 78.59
2026-06-19 09:15 | 241.33 | 243.28 | 241.06 | 418.41 | 418.79 | 419.63 | 24.7028 | 24.3204 | 26.5902 | 1.5083 | 1.439 | 1.446 | 1.432 | 1.907 | 0.564 | 1.758 | 50.01 | 3082 | 3204 | 3809 | 10095 | 103 | - - - | - - - | - - - | 3185 | 3204 | 3809 | 10095 | 903 | 1122 | 1344 | 3974 | -302 | - - - | - - - | - - - | 1205 | 1122 | 1344 | 3974 | 3727 | 3396 | 4056 | 11179 | -0.547 | # # # | # # # | # # # | 0.978 | 0.981 | 0.865 | 0.903 | # # # | # # # | # # # | # # # | 0.995 | 1 | 0.919 | 0.971 | # # # | 1.736 | 1.55 | 1.46 | 1.41 | 1.34 | 1.3 | 1.37 | 32.26 | 10.09 | 29.01 | 93.39
2026-06-19 09:25 | 241.68 | 243.48 | 241.24 | 418.87 | 419.18 | 420.05 | 36.49 | 35.872 | 39.2206 | 1.606 | 1.44 | 1.447 | 1.434 | 1.817 | 1.28 | 1.717 | 50.02 | 7078 | 7114 | 7890 | 22081 | 35 | - - - | - - - | - - - | 7113 | 7114 | 7890 | 22081 | 2589 | 2501 | 2597 | 7908 | -110 | - - - | - - - | - - - | 2699 | 2501 | 2597 | 7908 | 7724 | 7543 | 8316 | 23582 | -0.821 | -0.998 | # # # | # # # | 0.952 | 0.958 | 0.912 | 0.936 | # # # | # # # | # # # | # # # | 0.992 | 0.999 | 0.964 | 0.985 | # # # | 0.871 | 1.56 | 1.44 | 1.36 | 1.32 | 1.28 | 1.33 | 32.49 | 23.22 | 29.01 | 163.19
2026-06-19 09:35 | 243.29 | 244.39 | 242.3 | 421.01 | 421.03 | 422.26 | 2.0115 | 0.013 | 2.3122 | 0.4833 | 1.444 | 1.447 | 1.434 | 2.022 | 0 | 1.892 | 50.02 | -111 | 0 | 421 | 310 | 111 | 0 | - - - | - - - | - - - | 0 | 421 | 310 | 476 | - - - | 368 | 844 | -476 | - - - | - - - | - - - | - - - | - - - | 368 | 844 | 489 | 0 | 560 | 1049 | -0.228 | # # # | # # # | # # # | # # # | # # # | 0.751 | 0.296 | # # # | # # # | # # # | # # # | # # # | # # # | 0.818 | 0.818 | # # # | 2.735 | 1.55 | 1.45 | 1.41 | 1.29 | 1.34 | 1.4 | 34.9 | 0 | 30.24 | 3.48
2026-06-19 09:45 | 240.03 | 242.5 | 240.12 | 416.58 | 417.21 | 417.79 | 40.264 | 39.9986 | 43.3293 | 1.8266 | 1.437 | 1.446 | 1.436 | 1.747 | 1.519 | 1.684 | 49.97 | 8511 | 8645 | 9394 | 26551 | 14 | - - - | - - - | - - - | 8525 | 8645 | 9394 | 26551 | 3173 | 3003 | 3031 | 9307 | -50 | - - - | - - - | - - - | 3223 | 3003 | 3031 | 9307 | 9167 | 9152 | 9875 | 28194 | -0.922 | # # # | # # # | # # # | 0.941 | 0.95 | 0.936 | 0.942 | # # # | # # # | # # # | # # # | 0.991 | 1 | 0.982 | 0.991 | # # # | 0.587 | 1.9 | 1.63 | 1.59 | 1.61 | 1.49 | 1.64 | 30.59 | 27.76 | 28.66 | 346.43
2026-06-19 09:55 | 241.2 | 242.82 | 240.73 | 418.01 | 418.09 | 419.15 | 18.4517 | 18.1349 | 19.8397 | 1.0603 | 1.442 | 1.449 | 1.434 | 1.974 | 0.329 | 1.841 | 49.99 | 1668 | 1771 | 2273 | 5713 | 94 | - - - | - - - | - - - | 1762 | 1771 | 2273 | 5713 | 319 | 643 | 937 | 2635 | -368 | - - - | - - - | - - - | 687 | 643 | 937 | 2635 | 2273 | 1886 | 2488 | 6647 | -0.386 | # # # | # # # | # # # | 0.988 | 0.989 | 0.794 | 0.86 | # # # | # # # | # # # | # # # | 0.997 | 0.999 | 0.856 | 0.951 | # # # | 2.22 | 1.69 | 1.58 | 1.53 | 1.45 | 1.48 | 1.52 | 32.97 | 6.31 | 29.36 | 58.36
2026-06-19 10:05 | 241.57 | 243.15 | 241.03 | 418.51 | 418.71 | 419.76 | 1.9218 | 0.0145 | 2.4074 | 1.2867 | 1.443 | 1.449 | 1.433 | 2.017 | 0 | 1.811 | 49.99 | -145 | 0 | 469 | 324 | 145 | 0 | - - - | - - - | - - - | 0 | 469 | 324 | 440 | - - - | 340 | 780 | -440 | - - - | - - - | - - - | - - - | - - - | 340 | 780 | 464 | 0 | 580 | 1044 | -0.312 | # # # | # # # | # # # | # # # | # # # | 0.809 | 0.31 | # # # | # # # | # # # | # # # | # # # | # # # | 0.873 | 0.873 | # # # | 2.405 | 1.81 | 1.69 | 1.55 | 1.55 | 1.55 | 1.59 | 34.33 | 0 | 28.1 | 14.41
2026-06-19 10:15 | 241.72 | 243.17 | 241.04 | 418.66 | 418.79 | 419.83 | 2.0012 | 0.0145 | 2.2437 | 0.1515 | 1.438 | 1.447 | 1.43 | 1.979 | 0 | 1.862 | 49.99 | -118 | 0 | 423 | 305 | 118 | 0 | - - - | - - - | - - - | 0 | 423 | 305 | 469 | - - - | 335 | 804 | -469 | - - - | - - - | - - - | - - - | - - - | 335 | 804 | 484 | 0 | 541 | 1024 | -0.244 | # # # | # # # | # # # | # # # | # # # | 0.782 | 0.298 | # # # | # # # | # # # | # # # | # # # | # # # | 0.841 | 0.841 | # # # | 2.64 | 1.74 | 1.61 | 1.43 | 1.54 | 1.42 | 1.45 | 33.62 | 0 | 29.76 | 0.27
2026-06-19 10:25 | 242.49 | 243.96 | 241.82 | 420.08 | 420.13 | 421.14 | 2.0755 | 0.1245 | 2.5989 | 1.0435 | 1.438 | 1.447 | 1.43 | 2.042 | 0.06 | 1.844 | 49.97 | -118 | 1 | 482 | 365 | 128 | - - - | - - - | - - - | 10 | 1 | 482 | 365 | -408 | 3 | 375 | 847 | -438 | - - - | - - - | - - - | 30 | 3 | 375 | 847 | 488 | 3 | 613 | 1105 | -0.297 | # # # | # # # | # # # | 0.983 | 0.988 | 0.78 | 0.33 | # # # | # # # | # # # | # # # | 0.982 | 0.997 | 0.839 | 0.939 | # # # | 2.477 | 1.57 | 1.53 | 1.38 | 1.38 | 1.39 | 1.35 | 35.08 | 1.64 | 28.69 | 14.96
2026-06-19 10:35 | 244.69 | 246.26 | 244.09 | 423.97 | 424.04 | 425.05 | 29.6209 | 28.8912 | 31.6791 | 1.0678 | 1.438 | 1.442 | 1.429 | 1.898 | 0.827 | 1.795 | 50.01 | 4608 | 4644 | 5309 | 14561 | 63 | - - - | - - - | - - - | 4671 | 4644 | 5309 | 14561 | 1531 | 1632 | 1859 | 5537 | -257 | - - - | - - - | - - - | 1788 | 1632 | 1859 | 5537 | 5270 | 4924 | 5655 | 15849 | -0.607 | # # # | # # # | # # # | 0.967 | 0.972 | 0.838 | 0.919 | # # # | # # # | # # # | # # # | 0.996 | 0.999 | 0.895 | 0.963 | # # # | 1.655 | 1.53 | 1.41 | 1.33 | 1.3 | 1.27 | 1.3 | 34.25 | 15.75 | 29.66 | 125.96
2026-06-19 10:45 | 244.39 | 245.89 | 243.82 | 423.41 | 423.55 | 424.49 | 32.4175 | 31.7162 | 34.7936 | 1.4603 | 1.437 | 1.441 | 1.43 | 1.895 | 1.041 | 1.767 | 49.96 | 5630 | 5667 | 6414 | 17711 | 62 | - - - | - - - | - - - | 5692 | 5667 | 6414 | 17711 | 2025 | 2024 | 2188 | 6613 | -188 | - - - | - - - | - - - | 2213 | 2024 | 2188 | 6613 | 6307 | 6019 | 6795 | 19121 | -0.722 | # # # | # # # | # # # | 0.96 | 0.966 | 0.882 | 0.926 | # # # | # # # | # # # | # # # | 0.993 | 0.999 | 0.932 | 0.975 | # # # | 1.239 | 1.57 | 1.42 | 1.4 | 1.34 | 1.3 | 1.34 | 33 | 19.19 | 29.52 | 193.97
2026-06-19 10:55 | 244.08 | 245.82 | 243.57 | 423.03 | 423.2 | 424.1 | 2.073 | 0.016 | 2.4148 | 0.6038 | 1.436 | 1.442 | 1.427 | 2.028 | 0 | 1.875 | 49.98 | -142 | 0 | 459 | 317 | 142 | 0 | - - - | - - - | - - - | 0 | 459 | 317 | 485 | - - - | 367 | 852 | -485 | - - - | - - - | - - - | - - - | - - - | 367 | 852 | 506 | 0 | 588 | 1094 | -0.28 | # # # | # # # | # # # | # # # | # # # | 0.781 | 0.29 | # # # | # # # | # # # | # # # | # # # | # # # | 0.85 | 0.85 | # # # | 2.691 | 1.61 | 1.42 | 1.37 | 1.36 | 1.29 | 1.34 | 35.2 | 0 | 31.26 | 5.38
2026-06-19 11:05 | 244.04 | 245.71 | 243.51 | 422.92 | 423.08 | 423.99 | 2.0309 | 0.016 | 2.4892 | 1.1791 | 1.434 | 1.442 | 1.426 | 2.048 | 0.001 | 1.848 | 49.99 | -151 | 0 | 481 | 330 | 151 | 0 | - - - | - - - | - - - | 0 | 481 | 330 | 472 | - - - | 368 | 840 | -472 | - - - | - - - | - - - | - - - | - - - | 368 | 840 | 495 | 0 | 606 | 1101 | -0.305 | # # # | # # # | # # # | # # # | # # # | 0.794 | 0.3 | # # # | # # # | # # # | # # # | # # # | # # # | 0.857 | 0.857 | # # # | 2.549 | 1.51 | 1.46 | 1.33 | 1.32 | 1.3 | 1.29 | 36.55 | 0 | 29.8 | 16.37
2026-06-19 11:15 | 244.22 | 245.92 | 243.7 | 423.24 | 423.42 | 424.32 | 35.5862 | 34.8213 | 38.1081 | 1.2957 | 1.436 | 1.444 | 1.429 | 1.817 | 1.202 | 1.733 | 49.99 | 6775 | 6787 | 7550 | 21112 | 37 | - - - | - - - | - - - | 6812 | 6787 | 7550 | 21112 | 2449 | 2367 | 2501 | 7608 | -146 | - - - | - - - | - - - | 2595 | 2367 | 2501 | 7608 | 7441 | 7189 | 7970 | 22600 | -0.78 | # # # | # # # | # # # | 0.953 | 0.96 | 0.89 | 0.934 | # # # | # # # | # # # | # # # | 0.99 | 1 | 0.938 | 0.976 | # # # | 1.075 | 1.62 | 1.51 | 1.42 | 1.41 | 1.35 | 1.39 | 32.52 | 21.77 | 29.57 | 174.18
2026-06-19 11:25 | 244.18 | 245.79 | 243.64 | 423.09 | 423.25 | 424.25 | 25.3985 | 24.9177 | 27.3942 | 1.3186 | 1.437 | 1.443 | 1.428 | 1.957 | 0.641 | 1.813 | 49.96 | 3401 | 3488 | 4119 | 11007 | 86 | - - - | - - - | - - - | 3487 | 3488 | 4119 | 11007 | 1046 | 1240 | 1494 | 4385 | -302 | - - - | - - - | - - - | 1348 | 1240 | 1494 | 4385 | 4053 | 3703 | 4409 | 12165 | -0.542 | -1 | # # # | # # # | 0.975 | 0.979 | 0.83 | 0.905 | # # # | # # # | # # # | # # # | 0.995 | 1 | 0.891 | 0.962 | # # # | 1.828 | 1.48 | 1.34 | 1.29 | 1.24 | 1.21 | 1.23 | 35.28 | 11.7 | 29.9 | 88.68
2026-06-19 11:35 | 244.93 | 246.56 | 244.39 | 424.41 | 424.55 | 425.55 | 11.727 | 11.2875 | 12.6302 | 0.5199 | 1.438 | 1.445 | 1.428 | 2.017 | 0.125 | 1.914 | 50.06 | 611 | 706 | 1167 | 2484 | 99 | - - - | - - - | - - - | 710 | 706 | 1167 | 2484 | -185 | 257 | 622 | 1626 | -466 | - - - | - - - | - - - | 281 | 257 | 622 | 1626 | 1243 | 755 | 1355 | 3353 | -0.267 | # # # | # # # | # # # | 0.995 | 0.996 | 0.743 | 0.741 | # # # | # # # | # # # | # # # | 0.999 | 0.999 | 0.804 | 0.934 | # # # | 2.708 | 1.46 | 1.44 | 1.27 | 1.26 | 1.29 | 1.22 | 36.47 | 2.29 | 31.3 | 26.52
2026-06-19 11:45 | 244.31 | 246.13 | 243.95 | 423.47 | 423.79 | 424.67 | 41.9303 | 41.2062 | 45.1525 | 1.6817 | 1.434 | 1.44 | 1.426 | 1.74 | 1.719 | 1.682 | 49.98 | 9561 | 9565 | 10479 | 29605 | - - - | - - - | - - - | - - - | 9561 | 9565 | 10479 | 29605 | 3670 | 3360 | 3382 | 10412 | - - - | - - - | - - - | - - - | 3670 | 3360 | 3382 | 10412 | 10241 | 10138 | 11012 | 31391 | # # # | # # # | # # # | # # # | 0.934 | 0.944 | 0.952 | 0.943 | # # # | # # # | # # # | # # # | 0.987 | 0.999 | 0.998 | 0.995 | # # # | 0.352 | 1.55 | 1.38 | 1.3 | 1.32 | 1.2 | 1.25 | 31.07 | 30.55 | 29.43 | 261.52
2026-06-19 11:55 | 245.63 | 246.93 | 244.84 | 425.37 | 425.31 | 426.47 | 4.0284 | 3.323 | 4.3408 | 0.1142 | 1.434 | 1.443 | 1.422 | 2.055 | 0.013 | 1.968 | 49.95 | -44 | 63 | 478 | 498 | 108 | - - - | - - - | - - - | 64 | 63 | 478 | 498 | -486 | 18 | 428 | 989 | -515 | - - - | - - - | - - - | 29 | 18 | 428 | 989 | 597 | 71 | 649 | 1317 | -0.21 | # # # | # # # | # # # | 1 | 1 | 0.715 | 0.378 | # # # | # # # | # # # | # # # | 0.998 | 1 | 0.79 | 0.93 | # # # | 3.027 | 1.8 | 1.77 | 1.41 | 1.72 | 1.53 | 1.41 | 37.6 | 0.81 | 33.42 | 1.81
2026-06-19 12:05 | 245.88 | 246.49 | 244.5 | 425.15 | 424.83 | 426.26 | 2.1568 | 0.008 | 2.3308 | 0 | 1.427 | 1.432 | 1.424 | 2.042 | 0 | 1.971 | 50.03 | -105 | 0 | 406 | 301 | 105 | 0 | - - - | - - - | - - - | 0 | 406 | 301 | 520 | - - - | 400 | 920 | -520 | - - - | - - - | - - - | - - - | - - - | 400 | 920 | 530 | 0 | 570 | 1100 | -0.198 | # # # | # # # | # # # | # # # | # # # | 0.712 | 0.274 | # # # | # # # | # # # | # # # | # # # | # # # | 0.776 | 0.776 | # # # | 3.056 | 1.71 | 1.47 | 1.47 | 1.43 | 1.37 | 1.47 | 37.32 | 0 | 33.28 | # # #
2026-06-19 12:15 | 242.83 | 243.11 | 241.35 | 419.71 | 419.24 | 420.72 | 2.0268 | 0.008 | 2.1849 | 0 | 1.422 | 1.431 | 1.421 | 2.023 | 0 | 1.951 | 50.02 | -96 | 0 | 382 | 286 | 96 | 0 | - - - | - - - | - - - | 0 | 382 | 286 | 483 | - - - | 363 | 846 | -483 | - - - | - - - | - - - | - - - | - - - | 363 | 846 | 492 | 0 | 527 | 1020 | -0.195 | # # # | # # # | # # # | # # # | # # # | 0.725 | 0.28 | # # # | # # # | # # # | # # # | # # # | # # # | 0.787 | 0.787 | # # # | 2.958 | 1.09 | 0.99 | 1.06 | 0.87 | 0.84 | 0.85 | 34.4 | 0 | 32 | # # #
2026-06-19 12:25 | 242.86 | 243.08 | 241.31 | 419.7 | 419.16 | 420.73 | 2.0179 | 0.008 | 2.1757 | 0 | 1.422 | 1.433 | 1.422 | 2.028 | 0 | 1.953 | 50.02 | -96 | 0 | 380 | 285 | 96 | 0 | - - - | - - - | - - - | 0 | 380 | 285 | 481 | - - - | 362 | 842 | -481 | - - - | - - - | - - - | - - - | - - - | 362 | 842 | 490 | 0 | 525 | 1015 | -0.195 | # # # | # # # | # # # | # # # | # # # | 0.725 | 0.281 | # # # | # # # | # # # | # # # | # # # | # # # | 0.798 | 0.798 | # # # | 2.96 | 1.05 | 1 | 1.06 | 0.85 | 0.83 | 0.83 | 35.29 | 0 | 31.62 | # # #
2026-06-19 12:35 | 243.11 | 243.28 | 241.55 | 420.08 | 419.54 | 421.15 | 2.0366 | 0.008 | 2.1698 | 0 | 1.422 | 1.432 | 1.421 | 2.024 | 0 | 1.958 | 50.04 | -93 | 0 | 379 | 286 | 93 | 0 | - - - | - - - | - - - | 0 | 379 | 286 | 486 | - - - | 362 | 848 | -486 | - - - | - - - | - - - | - - - | - - - | 362 | 848 | 495 | 0 | 524 | 1019 | -0.188 | # # # | # # # | # # # | # # # | # # # | 0.724 | 0.281 | # # # | # # # | # # # | # # # | # # # | # # # | 0.788 | 0.788 | # # # | 2.962 | 1.05 | 0.97 | 1.06 | 0.85 | 0.82 | 0.83 | 35.55 | 0 | 31.75 | # # #
2026-06-19 12:45 | 243.11 | 243.29 | 241.53 | 420.08 | 419.54 | 421.12 | 2.0548 | 0.008 | 2.1767 | 0 | 1.422 | 1.434 | 1.422 | 2.03 | 0 | 1.962 | 50.01 | -97 | 0 | 381 | 284 | 97 | 0 | - - - | - - - | - - - | 0 | 381 | 284 | 490 | - - - | 363 | 853 | -490 | - - - | - - - | - - - | - - - | - - - | 363 | 853 | 500 | 0 | 526 | 1025 | -0.194 | # # # | # # # | # # # | # # # | # # # | 0.724 | 0.277 | # # # | # # # | # # # | # # # | # # # | # # # | 0.785 | 0.785 | # # # | 3.006 | 1.04 | 0.99 | 1.05 | 0.85 | 0.82 | 0.84 | 34.81 | 0 | 32.34 | # # #
2026-06-19 12:55 | 243.15 | 243.12 | 241.45 | 420 | 419.35 | 421.05 | 1.2588 | 0.008 | 1.3384 | 0 | 1.423 | 1.438 | 1.422 | 0.765 | 0 | 0.741 | 49.96 | -37 | 0 | 143 | 106 | 37 | 0 | - - - | - - - | - - - | 0 | 143 | 106 | 184 | - - - | 137 | 321 | -184 | - - - | - - - | - - - | - - - | - - - | 137 | 321 | 188 | 0 | 198 | 386 | -0.698 | # # # | # # # | # # # | # # # | # # # | 0.896 | 0.275 | # # # | # # # | # # # | # # # | # # # | # # # | 0.922 | 0.922 | # # # | 1.139 | 1.08 | 0.99 | 1.09 | 0.86 | 0.85 | 0.86 | 12.96 | 0 | 12.39 | # # #
2026-06-19 13:05 | 243.26 | 243.13 | 241.54 | 420.1 | 419.45 | 421.21 | 0.0069 | 0.008 | 0 | 0 | 1.424 | 1.44 | 1.423 | 0 | 0 | # # # | 49.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.07 | 1.01 | 1.1 | 0.86 | 0.85 | 0.85 | 0 | 0 | # # # | # # #
2026-06-19 13:15 | 243.15 | 242.95 | 241.41 | 419.84 | 419.22 | 420.97 | 0.0069 | 0.008 | 0 | 0 | 1.424 | 1.436 | 1.422 | 0 | 0 | # # # | 49.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.06 | 1.03 | 1.1 | 0.87 | 0.86 | 0.86 | 0 | 0 | # # # | # # #
2026-06-19 13:25 | 243.01 | 242.81 | 241.26 | 419.61 | 418.97 | 420.71 | 0.0069 | 0.008 | 0 | 0 | 1.424 | 1.435 | 1.422 | 0 | 0 | # # # | 49.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.07 | 0.99 | 1.08 | 0.86 | 0.84 | 0.84 | 0 | 0 | # # # | # # #
2026-06-19 13:35 | 243 | 242.78 | 241.19 | 419.57 | 418.87 | 420.67 | 0.0069 | 0.008 | 0 | 0 | 1.423 | 1.434 | 1.422 | 0 | 0 | # # # | 49.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.11 | 1.01 | 1.12 | 0.9 | 0.85 | 0.9 | 0 | 0 | # # # | # # #
2026-06-19 13:45 | 242.68 | 242.42 | 240.89 | 418.97 | 418.29 | 420.14 | 0.0069 | 0.008 | 0 | 0 | 1.424 | 1.435 | 1.423 | 0 | 0 | # # # | 49.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.1 | 1.03 | 1.11 | 0.9 | 0.85 | 0.9 | 0 | 0 | # # # | # # #
2026-06-19 13:55 | 242.31 | 242.09 | 240.53 | 418.34 | 417.71 | 419.51 | 0.0069 | 0.008 | 0 | 0 | 1.424 | 1.437 | 1.422 | 0 | 0 | # # # | 49.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.16 | 1.05 | 1.15 | 0.95 | 0.89 | 0.94 | 0 | 0 | # # # | # # #
2026-06-19 14:05 | 242.13 | 241.96 | 240.29 | 418.05 | 417.38 | 419.19 | 0.0069 | 0.008 | 0 | 0 | 1.425 | 1.439 | 1.423 | 0 | 0 | # # # | 49.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | - - - | 0 | 0 | 0 | 0 | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | # # # | 1.17 | 1.05 | 1.17 | 0.95 | 0.91 | 0.95 | 0 | 0 | # # # | # # #
2026-06-19 14:15 | 239.42 | 241.84 | 237.27 | 414.4 | 414.44 | 415.58 | 25.4624 | 25.308 | 27.3912 | 1.4932 | 1.429 | 1.454 | 1.429 | 1.385 | 0.591 | 1.291 | 49.93 | 3260 | 3378 | 3779 | 10416 | 52 | - - - | - - - | - - - | 3312 | 3378 | 3779 | 10416 | 1101 | 1201 | 1306 | 3950 | -171 | - - - | - - - | - - - | 1272 | 1201 | 1306 | 3950 | 3732 | 3589 | 4012 | 11333 | -0.725 | # # # | # # # | # # # | 0.974 | 0.98 | 0.912 | 0.919 | # # # | # # # | # # # | # # # | 0.993 | 0.999 | 0.953 | 0.981 | # # # | 1.057 | 1.91 | 1.57 | 1.64 | 1.58 | 1.42 | 1.58 | 24.2 | 10.65 | 20.5 | 71.57
2026-06-19 14:25 | 239.64 | 243.3 | 236.31 | 414.68 | 414.94 | 415.93 | 36.6189 | 36.3219 | 39.3566 | 1.8086 | 1.433 | 1.463 | 1.435 | 1.819 | 1.264 | 1.716 | 49.94 | 6964 | 7116 | 7677 | 21756 | 32 | - - - | - - - | - - - | 6996 | 7116 | 7677 | 21756 | 2572 | 2530 | 2561 | 7889 | -113 | - - - | - - - | - - - | 2685 | 2530 | 2561 | 7889 | 7613 | 7554 | 8103 | 23270 | -0.805 | # # # | # # # | # # # | 0.952 | 0.958 | 0.909 | 0.935 | # # # | # # # | # # # | # # # | 0.995 | 0.997 | 0.956 | 0.983 | # # # | 0.882 | 2.05 | 1.73 | 1.9 | 1.7 | 1.61 | 1.76 | 32.08 | 23.23 | 28.13 | 225.2
2026-06-19 14:35 | 241.04 | 243.62 | 237.7 | 416.6 | 416.57 | 417.83 | 5.6683 | 5.2005 | 6.2033 | 0.8077 | 1.436 | 1.45 | 1.433 | 1.997 | 0.025 | 1.844 | 49.99 | 28 | 133 | 557 | 718 | 105 | - - - | - - - | - - - | 133 | 133 | 557 | 718 | -384 | 55 | 395 | 954 | -444 | - - - | - - - | - - - | 60 | 55 | 395 | 954 | 604 | 146 | 692 | 1442 | -0.243 | # # # | # # # | # # # | 0.998 | 0.998 | 0.769 | 0.498 | # # # | # # # | # # # | # # # | 0.999 | 1 | 0.824 | 0.941 | # # # | 2.555 | 1.58 | 1.43 | 1.45 | 1.3 | 1.3 | 1.33 | 33.23 | 0.36 | 28.39 | 9.16