## UBAP BERSIH GD.A
A. | Unit Beban Alat Plumbing Gedung A |  |  |  | Proyek |  |  |  | KP
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Jumlah Alat Plumbing Ap | Unit Beban Alat Plumbing | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas) | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas)
LANTAI 1
| 1 | Kloset Tangki Gelontor | 8 |  | 5 |  | 40 |  | 5 |  | 40
| 2 | Keran | 8 |  | 2 | 16 |  |  | 2 | 16
| 3 | Bak Cuci Tangan | 21 | 20 | 2 | 42 |  | 40 | 2 | 42 |  | 40
| 4 | Bak Cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 5 | Shower | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 6 | Sink Kran Klinik | 4 | 4 | 3 | 12 |  | 12 | 3 | 12 |  | 12
| 7 | Scrub | 6 | 6 | 4 | 24 |  | 24 | 4 | 24 |  | 24
| 8 | Bak Pel | 1 |  | 3 | 3 |  | 0 | 3 | 3 |  | 0
| 9 | Sink Lab | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
[5 empty] | TOTAL LANTAI 1 | 109 | 40 | 88 | TOTAL LANTAI 1 | 109 | 40 | 88
LANTAI 2
| 1 | Kloset Tangki Gelontor | 13 |  | 5 |  | 65 |  | 5 |  | 65
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 15 |  | 2 | 30 |  |  | 2 | 30
| 4 | Bak Cuci Tangan | 14 | 14 | 2 | 28 |  | 28 | 2 | 28 |  | 28
| 5 | Peturasan Katup Gelontor | 3 |  | 5 | 15 |  |  | 5 | 15
| 6 | Bak Cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 7 | Shower | 3 | 3 | 2 | 6 |  | 6 | 2 | 6 |  | 6
| 8 | Sink Kran Klinik | 1 | 1 | 3 | 3 |  | 3 | 3 | 3 |  | 3
| 9 | Scrub | 1 | 1 | 4 | 4 |  | 4 | 4 | 4 |  | 4
| 10 | Sink Lab | 15 | 15 | 2 | 30 |  | 30 | 2 | 30 |  | 30
| 11 | Sink Cuci Muka | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
[5 empty] | TOTAL LANTAI 2 | 142 | 65 | 77 | TOTAL LANTAI 2 | 142 | 65 | 77
LANTAI 3
| 1 | Kloset Tangki Gelontor | 21 |  | 5 |  | 105 |  | 5 |  | 105
| 2 | Keran | 21 |  | 2 | 42 |  |  | 2 | 42
| 3 | Bak Cuci Tangan | 52 | 35 | 2 | 104 |  | 70 | 2 | 104 |  | 70
| 4 | Peturasan Katup Gelontor | 4 |  | 5 | 20 |  |  | 5 | 20
| 5 | Shower | 4 | 2 | 2 | 8 |  | 4 | 2 | 8 |  | 4
| 6 | Sink Kran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
[5 empty] | TOTAL LANTAI 3 | 180 | 105 | 80 | TOTAL LANTAI 3 | 180 | 105 | 80
LANTAI 4
| 1 | Kloset Tangki Gelontor | 14 |  | 5 |  | 70 |  | 5 |  | 70
| 2 | Keran | 14 |  | 2 | 28 |  |  | 2 | 28
| 3 | Bak Cuci Tangan | 61 | 38 | 2 | 122 |  | 76 | 2 | 122 |  | 76
| 4 | Peturasan Katup Gelontor | 4 |  | 5 | 20 |  |  | 5 | 20
| 5 | Sink Kran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
[5 empty] | TOTAL LANTAI 4 | 176 | 70 | 82 | TOTAL LANTAI 4 | 176 | 70 | 82
LANTAI 5
| 1 | Kloset Tangki Gelontor | 14 |  | 5 |  | 70 |  | 5 |  | 70
| 2 | Keran | 14 |  | 2 | 28 |  |  | 2 | 28
| 3 | Bak Cuci Tangan | 8 | 2 | 2 | 16 |  | 4 | 2 | 16 |  | 4
| 4 | Peturasan Katup Gelontor | 4 |  | 5 | 20 |  |  | 5 | 20
| 5 | Bak Cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
[5 empty] | TOTAL LANTAI 5 | 68 | 70 | 8 | TOTAL LANTAI 5 | 68 | 70 | 8
LANTAI 6
| 1 | Kloset Tangki Gelontor | 14 |  | 5 |  | 70 |  | 5 |  | 70
| 2 | Keran | 14 |  | 2 | 28 |  |  | 2 | 28
| 3 | Bak Cuci Tangan | 8 | 2 | 2 | 16 |  | 4 | 2 | 16 |  | 4
| 4 | Peturasan Katup Gelontor | 4 |  | 5 | 20 |  |  | 5 | 20
| 5 | Sink Kran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| TOTAL LANTAI 6 |  |  |  |  | 70 | 70 | 10 | TOTAL LANTAI 6 | 70 | 70 | 10
| TOTAL SISTEM 1 (lt. 1 - lt 3) |  |  |  |  | 431 | 210 |  | TOTAL SISTEM 1 (lt. 1 - lt 3) | 431 | 210
| TOTAL SISTEM 2 (lt. 4 - lt 6) |  |  |  |  | 314 | 210 |  | TOTAL SISTEM 2 (lt. 4 - lt 6) | 314 | 210
| TOTAL |  |  |  |  | 745 | 420 | 345 | TOTAL | 745 | 420 | 345
Catatan :
1) SNI 8153 : 2015 Halaman 30 dan 31 (Tabel 3), dan 33 (Tabel 5)
2) SNI 03-7065-2005 Halaman 7 (Tabel 7)

## UBAP BERSIH GD.B
A. | Unit Beban Alat Plumbing Gedung B |  |  |  | Proyek |  |  |  | KP
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Jumlah Alat Plumbing AP | Unit Beban Alat Plumbing | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas) | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas)
LANTAI BASEMENT
| 1 | Kloset Tangki Gelontor | 8 |  | 5 |  | 40 |  | 5 |  | 40
| 2 | Keran | 8 |  | 2 | 16 |  |  | 2 | 16
| 3 | Bak Cuci Tangan | 5 | 2 | 2 | 10 |  | 4 | 2 | 10 |  | 4
| 4 | Shower | 8 | 8 | 2 | 16 |  | 16 | 2 | 16 |  | 16
| TOTAL LANTAI BASEMENT |  |  |  |  | 42 | 40 | 20 | TOTAL LANTAI BASEMENT | 42 | 40 | 20
LANTAI 1
| 1 | Kloset Tangki Gelontor | 6 |  | 5 |  | 30 |  | 5 |  | 30
| 2 | Keran | 12 |  | 2 | 24 |  |  | 2 | 24
| 3 | Bak Cuci Tangan | 9 | 5 | 2 | 18 |  | 10 | 2 | 18 |  | 10
| 4 | Peturasan katup Gelontor | 1 |  | 5 | 5 |  |  | 5 | 5
| 5 | Bak Cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 6 | Kloset katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| TOTAL LANTAI 1 |  |  |  |  | 71 | 30 | 14 | TOTAL LANTAI 1 | 71 | 30 | 14
LANTAI 2
| 1 | Kloset Tangki Gelontor | 5 |  | 5 |  | 25 |  | 5 |  | 25
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 11 |  | 2 | 22 |  |  | 2 | 22
| 4 | Bak Cuci Tangan | 30 | 30 | 2 | 60 |  | 60 | 2 | 60 |  | 60
| 5 | Peturasan katup Gelontor | 2 | 2 | 5 | 10 |  | 10 | 5 | 10 |  | 10
| 6 | Sink Keran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| TOTAL LANTAI 2 |  |  |  |  | 118 | 25 | 76 | TOTAL LANTAI 2 | 118 | 25 | 76
LANTAI PARKIR P2A-P3B
| 1 | Kloset Tangki Gelontor | 1 |  | 5 |  | 5 |  | 5 |  | 5
| 2 | Keran | 3 |  | 2 | 6 |  |  | 2 | 6
| TOTAL LANTAI PARKIR P2A-P3B |  |  |  |  | 6 | 5 |  | TOTAL LANTAI PARKIR P2A-P3B | 6 | 5
LANTAI 3
| 1 | Kloset Tangki Gelontor | 5 |  | 5 |  | 25 |  | 5 |  | 25
| 2 | Keran | 5 |  | 2 | 10 |  |  | 2 | 10
| 3 | Bak Cuci Tangan | 2 | 1 | 2 | 4 |  | 2 | 2 | 4 |  | 2
| 4 | Scrub | 6 | 6 | 4 | 24 |  | 24 | 4 | 24 |  | 24
| 5 | Sink keran Klinik/sphk | 1 |  | 3 | 3 |  |  | 3 | 3
| 6 | Shower | 4 | 4 | 2 | 8 |  | 8 | 2 | 8 |  | 8
| TOTAL LANTAI 3 |  |  |  |  | 49 | 25 | 34 | TOTAL LANTAI 3 | 49 | 25 | 34
LANTAI PARKIR P3A-P4B
| 1 | Kloset Tangki Gelontor | 1 |  | 5 |  | 5 |  | 5 |  | 5
| 2 | Keran | 3 |  | 2 | 6 |  |  | 2 | 6
| TOTAL LANTAI PARKIR P3A-P4B |  |  |  |  | 6 | 5 |  | TOTAL LANTAI PARKIR P3A-P4B | 6 | 5
LANTAI 4
| 1 | Kloset Tangki Gelontor | 5 |  | 5 |  | 25 |  | 5 |  | 25
| 2 | Keran | 5 |  | 2 | 10 |  |  | 2 | 10
| 3 | Bak Cuci Tangan | 2 | 1 | 2 | 4 |  | 2 | 2 | 4 |  | 2
| 4 | Sink keran Klinik/sphk | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 5 | Shower | 4 | 4 | 2 | 8 |  | 8 | 2 | 8 |  | 8
| TOTAL LANTAI 4 |  |  |  |  | 28 | 25 | 16 | TOTAL LANTAI 4 | 28 | 25 | 16
LANTAI PARKIR P5A-P6B
| 1 | Kloset Tangki Gelontor | 1 |  | 5 |  | 5 |  | 5 |  | 5
| 2 | Keran | 3 |  | 2 | 6 |  |  | 2 | 6
| TOTAL LANTAI PARKIR P5A-P6B |  |  |  |  | 6 | 5 |  | TOTAL LANTAI PARKIR P5A-P6B | 6 | 5
LANTAI 5
| 1 | Kloset Tangki Gelontor | 5 |  | 5 |  | 25 |  | 5 |  | 25
| 2 | Keran | 5 |  | 2 | 10 |  |  | 2 | 10
| 3 | Bak Cuci Tangan | 5 | 4 | 2 | 10 |  | 8 | 2 | 10 |  | 8
| 4 | Sink keran Klinik/sphk | 7 | 3 | 3 | 21 |  | 9 | 3 | 21 |  | 9
| TOTAL LANTAI 5 |  |  |  |  | 41 | 25 | 17 | TOTAL LANTAI 5 | 41 | 25 | 17
LANTAI PARKIR P6B-P7B
| 1 | Kloset Tangki Gelontor | 1 |  | 5 |  | 5 |  | 5 |  | 5
| 2 | Keran | 3 |  | 2 | 6 |  |  | 2 | 6
| TOTAL LANTAI PARKIR P6B-P7B |  |  |  |  | 6 | 5 |  | TOTAL LANTAI PARKIR P6B-P7B | 6 | 5
LANTAI 6
| 1 | Kloset Tangki Gelontor | 9 |  | 5 |  | 45 |  | 5 |  | 45
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 15 |  | 2 | 30 |  |  | 2 | 30
| 4 | Peturasan Katup Gelontor | 1 |  | 5 | 5 |  |  | 5 | 5
| 5 | Bak Cuci Tangan | 12 | 10 | 2 | 24 |  | 20 | 2 | 24 |  | 20
| 6 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| 7 | Bak cuci Piring | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
| 8 | Shower | 2 | 10 | 2 | 4 |  | 20 | 2 | 4 |  | 20
| TOTAL LANTAI 6 |  |  |  |  | 88 | 45 | 42 | TOTAL LANTAI 6 | 88 | 45 | 42
LANTAI 7
| 1 | Kloset Tangki Gelontor | 22 |  | 5 |  | 110 |  | 5 |  | 110
| 2 | Keran | 25 |  | 2 | 50 |  |  | 2 | 50
| 3 | Bak Cuci Tangan | 29 | 25 | 2 | 58 |  | 50 | 2 | 58 |  | 50
| 4 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| 5 | Sink keran Klinik/sphk | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 7 | Shower | 20 | 20 | 2 | 40 |  | 40 | 2 | 40 |  | 40
| TOTAL LANTAI 7 |  |  |  |  | 161 | 110 | 100 | TOTAL LANTAI 7 | 161 | 110 | 100
LANTAI 7 B1 - LANTAI 9 B2
| 1 | Kloset Tangki Gelontor | 20 |  | 5 |  | 100 |  | 5 |  | 100
| 2 | Kloset Katup Gelontor | 3 |  | 10 | 30 |  |  | 10 | 30
| 3 | Keran | 23 |  | 2 | 46 |  |  | 2 | 46
| 4 | Bak Cuci Tangan | 19 | 18 | 2 | 38 |  | 36 | 2 | 38 |  | 36
| 5 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| 6 | Bak cuci Piring | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
| 7 | Shower | 15 | 15 | 2 | 30 |  | 30 | 2 | 30 |  | 30
| TOTAL LANTAI 7 B1 - LANTAI 9 B2 |  |  |  |  | 149 | 100 | 68 | TOTAL LANTAI 7 B1-LANTAI 9 B2 | 149 | 100 | 68
LANTAI 8
| 1 | Kloset Tangki Gelontor | 18 |  | 5 |  | 90 |  | 5 |  | 90
| 2 | Keran | 21 |  | 2 | 42 |  |  | 2 | 42
| 3 | Bak Cuci Tangan | 22 | 21 | 2 | 44 |  | 42 | 2 | 44 |  | 42
| 4 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| 5 | Sink keran Klinik/sphk | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 7 | Shower | 16 | 16 | 2 | 32 |  | 32 | 2 | 32 |  | 32
| TOTAL LANTAI 8 |  |  |  |  | 131 | 90 | 84 | TOTAL LANTAI 8 | 131 | 90 | 84
LANTAI 8 B1 - LANTAI 10 B2
| 1 | Kloset Tangki Gelontor | 13 |  | 5 |  | 65 |  | 5 |  | 65
| 2 | Kloset Katup Gelontor | 3 |  | 10 | 30 |  |  | 10 | 30
| 3 | Keran | 27 |  | 2 | 54 |  |  | 2 | 54
| 4 | Bak Cuci Tangan | 15 | 15 | 2 | 30 |  | 30 | 2 | 30 |  | 30
| 5 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| 6 | Bak cuci Piring | 5 | 5 | 2 | 10 |  | 10 | 2 | 10 |  | 10
| 7 | Shower | 2 | 8 | 2 | 4 |  | 16 | 2 | 4 |  | 16
| TOTAL LANTAI 8 B1 - LANTAI 10 B2 |  |  |  |  | 131 | 65 | 56 | TOTAL LANTAI 8 B1 - LANTAI 10 B2 | 131 | 65 | 56
LANTAI 9
| 1 | Kloset Tangki Gelontor | 18 |  | 5 |  | 90 |  | 5 |  | 90
| 2 | Keran | 21 |  | 2 | 42 |  |  | 2 | 42
| 3 | Bak Cuci Tangan | 22 | 21 | 2 | 44 |  | 42 | 2 | 44 |  | 42
| 4 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| 5 | Sink keran Klinik/sphk | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 7 | Shower | 16 | 16 | 2 | 32 |  | 32 | 2 | 32 |  | 32
| TOTAL LANTAI 9 |  |  |  |  | 131 | 90 | 84 | TOTAL LANTAI 9 | 131 | 90 | 84
LANTAI 9 B1 - LANTAI 11 B2
| 1 | Kloset Tangki Gelontor | 7 |  | 5 |  | 35 |  | 5 |  | 35
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 9 |  | 2 | 18 |  |  | 2 | 18
| 4 | Bak Cuci Tangan | 5 | 1 | 2 | 10 |  | 2 | 2 | 10 |  | 2
| 5 | Peturasan katup Gelontor | 3 |  | 5 | 15 |  |  | 5 | 15
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| TOTAL LANTAI 9 B1 - LANTAI 11 B2 |  |  |  |  | 67 | 35 | 6 | TOTAL LANTAI 9 B1 - LANTAI 11 B2 | 67 | 35 | 6
LANTAI 10
| 1 | Kloset Tangki Gelontor | 21 |  | 5 |  | 105 |  | 5 |  | 105
| 2 | Keran | 24 |  | 2 | 48 |  |  | 2 | 48
| 3 | Bak Cuci Tangan | 34 | 23 | 2 | 68 |  | 46 | 2 | 68 |  | 46
| 4 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| 5 | Sink keran Klinik/sphk | 18 | 18 | 3 | 54 |  | 54 | 3 | 54 |  | 54
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 7 | Shower | 19 | 19 | 2 | 38 |  | 38 | 2 | 38 |  | 38
| TOTAL LANTAI 10 |  |  |  |  | 215 | 105 | 142 | TOTAL LANTAI 10 | 215 | 105 | 142
| TOTAL SISTEM 1 (lt.bs-lt.6) |  |  |  |  | 461 | 235 |  | TOTAL SISTEM 1 (lt. bs - lt.6) | 461 | 235
| TOTAL SISTEM 2 (lt.7-lt.10) |  |  |  |  | 824 | 595 |  | TOTAL SISTEM 2 (lt.7 - lt.10) | 985 | 485
| TOTAL |  |  |  |  | 1446 | 830 | 759 |  | 1446 | 830 | 759
Catatan :
1) SNI 8153 : 2015 Halaman 30 dan 31 (Tabel 3), dan 33 (Tabel 5)
2) SNI 03-7065-2005 Halaman 7 (Tabel 7)
Note on D23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dari 18
Note on D132: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dari 2
Note on D133: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dari 1

## UBAP Bersih GD.C
A. | Unit Beban Alat Plumbing Gedung C |  |  |  | Proyek |  |  |  | KP
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Jumlah Alat Plumbing AP | Unit Beban Alat Plumbing | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas) | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas)
LANTAI BASEMENT
| 1 | Kloset Tangki Gelontor | 13 |  | 5 |  | 65 |  | 5 |  | 65
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 19 |  | 2 | 38 |  |  | 2 | 38
| 4 | Bak Cuci Tangan | 12 | 11 | 2 | 24 |  | 22 | 2 | 24 |  | 22
| 5 | Peturasan Katup Gelontor | 2 |  | 5 | 10 |  |  | 5 | 10
| 6 | Sink Kran Klinik | 6 | 5 | 2 | 18 |  | 15 | 3 | 18 |  | 15
| 7 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| 8 | Shower | 6 | 6 | 3 | 18 |  | 18 | 2 | 12 |  | 12
| TOTAL LANTAI BASEMENT |  |  |  |  | 131 | 65 | 55 | TOTAL LANTAI BASEMENT | 125 | 65 | 49
LANTAI 1
| 1 | Kloset Tangki Gelontor | 5 |  | 5 |  | 25 |  | 5 |  | 25
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 11 |  | 2 | 22 |  |  | 2 | 22
| 4 | Bak Cuci Tangan | 6 | 2 | 2 | 12 |  | 4 | 2 | 12 |  | 4
| 5 | Peturasan Katup Gelontor | 1 |  | 5 | 5 |  |  | 5 | 5
| 6 | Bak Cuci Piring | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
| 7 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI 1 |  |  |  |  | 64 | 25 | 6 | TOTAL LANTAI 1 | 64 | 25 | 6
LANTAI P1A-P2B
| 1 | Kloset Tangki Gelontor | 1 |  | 5 |  | 5 |  | 5 |  | 5
| 2 | Keran | 3 |  | 2 | 6 |  |  | 2 | 6
| TOTAL LANTAI P1A-P2B |  |  |  |  | 6 | 5 |  | TOTAL LANTAI P1A-P2B | 6 | 5 | 0
LANTAI 2
| 1 | Kloset Tangki Gelontor | 13 |  | 5 |  | 65 |  | 5 |  | 65
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 15 |  | 2 | 30 |  |  | 2 | 30
| 4 | Bak Cuci Tangan | 32 | 29 | 2 | 64 |  | 58 | 2 | 64 |  | 58
| 5 | Peturasan Katup Gelontor | 2 | 2 | 5 | 10 |  | 10 | 5 | 10 |  | 10
| 6 | Bak Cuci Piring | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
| 7 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI 2 |  |  |  |  | 129 | 65 | 70 | TOTAL LANTAI 2 | 129 | 65 | 70
LANTAI 3
| 1 | Kloset Tangki Gelontor | 7 |  | 5 |  | 35 |  | 5 |  | 35
| 2 | Keran | 9 |  | 2 | 18 |  |  | 2 | 18
| 3 | Bak Cuci Tangan | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
| 4 | Shower | 3 | 3 | 2 | 6 |  | 6 | 2 | 6 |  | 6
| 5 | Sink Kran Klinik | 2 | 2 | 2 | 6 |  | 6 | 3 | 6 |  | 6
| 6 | Scrub | 10 | 10 | 4 | 40 |  | 40 | 4 | 40 |  | 40
| TOTAL LANTAI 3 |  |  |  |  | 72 | 35 | 54 | TOTAL LANTAI 3 | 72 | 35 | 54
LANTAI P4A-P5B
| 1 | Kloset Tangki Gelontor | 2 |  | 5 |  | 10 |  | 5 |  | 10
| 2 | Keran | 2 |  | 2 | 4 |  |  | 2 | 4
| 3 | Bak Cuci Tangan | 3 | 3 | 2 | 6 |  | 6 | 2 | 6 |  | 6
| 4 | Bak Cuci Piring | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
| 5 | Shower | 2 | 2 | 2 | 2 |  | 4 | 2 | 4 |  | 4
| 6 | Sink Kran Klinik | 8 | 8 | 2 | 24 |  | 24 | 3 | 24 |  | 24
| 7 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI P4A-P5B |  |  |  |  | 41 | 10 | 36 | TOTAL LANTAI P4A-P5B | 43 | 10 | 36
LANTAI 4
| 1 | Kloset Tangki Gelontor | 11 |  | 5 |  | 55 |  | 5 |  | 55
| 2 | Keran | 13 |  | 2 | 26 |  |  | 2 | 26
| 3 | Bak Cuci Tangan | 9 | 3 | 2 | 18 |  | 6 | 2 | 18 |  | 6
| 4 | Bak Cuci Piring | 1 | 1 | 2 | 2 |  |  | 2 | 2
| 5 | Sink Kran Klinik | 6 | 3 | 2 | 18 |  | 9 | 3 | 18 |  | 9
| 6 | Bak Pel | 3 |  | 3 | 9 |  |  | 3 | 9
| TOTAL LANTAI 4 |  |  |  |  | 73 | 55 | 15 | TOTAL LANTAI 4 | 73 | 55 | 15
LANTAI 5
| 1 | Kloset Tangki Gelontor | 11 |  | 5 |  | 55 |  | 5 |  | 55
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 19 |  | 2 | 38 |  |  | 2 | 38
| 4 | Bak Cuci Tangan | 36 | 34 | 2 | 72 |  | 68 | 2 | 72 |  | 68
| 5 | Peturasan Katup Gelontor | 1 |  | 5 | 5 |  |  | 5 | 5
| 6 | Sink Kran Klinik | 1 | 1 | 2 | 3 |  | 3 | 3 | 3 |  | 3
| 7 | Bak Pel | 3 |  | 3 | 9 |  |  | 3 | 9
| TOTAL LANTAI 5 |  |  |  |  | 147 | 55 | 71 | TOTAL LANTAI 5 | 147 | 55 | 71
LANTAI P7A
| 1 | Kloset Tangki Gelontor | 2 |  | 5 |  | 10 |  | 5 |  | 10
| 2 | Keran | 3 |  | 2 | 6 |  |  | 2 | 6
| 3 | Bak Cuci Tangan | 5 | 4 | 2 | 10 |  | 8 | 2 | 10 |  | 8
| 4 | Bak Cuci Piring | 1 |  | 2 | 2 |  |  | 2 | 2
| 5 | Sink Kran Klinik | 3 |  | 2 | 9 |  |  | 3 | 9
| TOTAL LANTAI P7A |  |  |  |  | 27 | 10 | 8 | TOTAL LANTAI P7A | 27 | 10 | 8
LANTAI 6
| 1 | Kloset Tangki Gelontor | 40 |  | 5 |  | 200 |  | 5 |  | 200
| 2 | Keran | 81 | 28 | 2 | 162 |  | 56 | 2 | 162 |  | 56
| 3 | Bak Cuci Tangan | 44 | 37 | 2 | 88 |  | 74 | 2 | 88 |  | 74
| 4 | Peturasan Katup Gelontor | 2 |  | 5 | 10 |  |  | 5 | 10
| 5 | Bak Cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 6 | Shower | 35 | 35 | 2 | 68 |  | 70 | 2 | 70 |  | 70
| 7 | Sink Kran Klinik | 2 | 2 | 2 | 6 |  | 6 | 3 | 6 |  | 6
| 8 | Bak Pel | 3 |  | 3 | 9 |  |  | 3 | 9
| TOTAL LANTAI 6 |  |  |  |  | 347 | 200 | 210 | TOTAL LANTAI 6 | 349 | 200 | 210
LANTAI 7
| 1 | Kloset Tangki Gelontor | 38 |  | 5 |  | 190 |  | 5 |  | 190
| 2 | Kloset Katup Gelontor | 3 |  | 10 | 30 |  |  | 10 | 30
| 3 | Keran | 44 |  | 2 | 88 |  |  | 2 | 88
| 4 | Bak Cuci Tangan | 44 | 39 | 2 | 88 |  | 78 | 2 | 88 |  | 78
| 5 | Peturasan Katup Gelontor | 2 |  | 5 | 10 |  |  | 5 | 10
| 6 | Bak Cuci Piring | 3 | 3 | 2 | 6 |  | 6 | 2 | 6 |  | 6
| 7 | Shower | 31 | 31 | 2 | 62 |  | 62 | 2 | 62 |  | 62
| 8 | Sink Kran Klinik | 2 | 2 | 2 | 6 |  | 6 | 3 | 6 |  | 6
| 9 | Bak Pel | 2 |  | 3 | 6 |  |  | 3 | 6
| TOTAL LANTAI 7 |  |  |  |  | 296 | 190 | 152 | TOTAL LANTAI 7 | 296 | 190 | 152
LANTAI 8
| 1 | Kloset Tangki Gelontor | 31 |  | 5 |  | 155 |  | 5 |  | 155
| 2 | Kloset Katup Gelontor | 3 |  | 10 | 30 |  |  | 10 | 30
| 3 | Keran | 41 |  | 2 | 82 |  |  | 2 | 82
| 4 | Bak Cuci Tangan | 39 | 32 | 2 | 78 |  | 64 | 2 | 78 |  | 64
| 5 | Peturasan Katup Gelontor | 3 |  | 5 | 15 |  |  | 5 | 15
| 6 | Bak Cuci Piring | 6 | 6 | 2 | 10 |  | 12 | 2 | 12 |  | 12
| 7 | Shower | 25 | 25 | 2 | 50 |  | 50 | 2 | 50 |  | 50
| 8 | Sink Kran Klinik | 2 | 2 | 2 | 6 |  | 6 | 3 | 6 |  | 6
| 9 | Bak Pel | 2 |  | 3 | 6 |  |  | 3 | 6
| TOTAL LANTAI 8 |  |  |  |  | 277 | 155 | 132 | TOTAL LANTAI 8 | 279 | 155 | 132
LANTAI 9
| 1 | Kloset Tangki Gelontor | 25 |  | 5 |  | 125 |  | 5 |  | 125
| 2 | Kloset Katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 30 |  | 2 | 60 |  |  | 2 | 60
| 4 | Bak Cuci Tangan | 30 | 22 | 2 | 60 |  | 44 | 2 | 60 |  | 44
| 5 | Peturasan Katup Gelontor | 3 |  | 5 | 15 |  |  | 5 | 15
| 6 | Bak Cuci Piring | 4 | 4 | 2 | 8 |  | 8 | 2 | 8 |  | 8
| 7 | Shower | 16 | 16 | 2 | 32 |  | 32 | 2 | 32 |  | 32
| 8 | Sink Kran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 9 | Bak Pel | 2 |  | 3 | 6 |  | 0 | 3 | 6
| TOTAL LANTAI 9 |  |  |  |  | 207 | 125 | 90 | TOTAL LANTAI 9 | 207 | 125 | 90
LANTAI 10
| 1 | Kloset Tangki Gelontor | 21 |  | 5 |  | 105 |  | 5 |  | 105
| 2 | Keran | 24 |  | 2 | 48 |  |  | 2 | 48
| 3 | Bak Cuci Tangan | 26 | 23 | 2 | 52 |  | 46 | 2 | 52 |  | 46
| 4 | Bak Cuci Piring | 8 | 2 | 2 | 16 |  | 4 | 2 | 16 |  | 4
| 5 | Shower | 19 | 19 | 2 | 38 |  | 38 | 2 | 38 |  | 38
| 6 | Sink Kran Klinik | 18 | 18 | 3 | 6 |  | 54 | 3 | 54 |  | 54
| 7 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI 10 |  |  |  |  | 163 | 105 | 142 | TOTAL LANTAI 10 | 211 | 105 | 142
| TOTAL SISTEM 1 (lt.bs-lt.6) |  |  |  |  | 1019 | 525 |  |  | 1035 | 525 | 519
| TOTAL SISTEM 2 (lt.7-lt.10) |  |  |  |  | 943 | 575 |  |  | 993 | 575 | 516
| TOTAL |  |  |  |  | 1962 | 1100 | 1033 |  | 2028 | 1100 | 1035
Catatan :
1) SNI 8153 : 2015 Halaman 30 dan 31 (Tabel 3), dan 33 (Tabel 5)
2) SNI 03-7065-2005 Halaman 7 (Tabel 7)

## UBAP BERSIH GD.D
A. | Unit Beban Alat Plumbing Gedung D |  |  |  | Proyek |  |  |  | KP
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Jumlah Alat Plumbing AP | Unit Beban Alat Plumbing | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas) | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas)
LANTAI BASEMENT
| 1 | Kloset Tangki Gelontor | 27 |  | 5 |  | 135 |  | 5 |  | 135
| 2 | Keran | 27 |  | 2 | 54 |  |  | 2 | 54
| 3 | Bak Cuci Tangan | 33 | 20 | 2 | 66 |  | 40 | 2 | 66 |  | 40
| 4 | Shower | 15 | 15 | 4 | 60 |  | 60 | 2 | 30 |  | 30
| 5 | Bak Pel | 2 |  | 3 | 6 |  |  | 3 | 6
| TOTAL LANTAI BASEMENT |  |  |  |  | 186 | 135 | 100 | TOTAL LANTAI BASEMENT | 156 | 135 | 70
LANTAI 1
| 1 | Kloset Tangki Gelontor | 6 |  | 5 |  | 30 |  | 5 |  | 30
| 2 | Kloset katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 12 |  | 2 | 24 |  |  | 2 | 24
| 4 | Bak Cuci Tangan | 12 | 7 | 2 | 24 |  | 14 | 2 | 24 |  | 14
| 5 | Bak Cuci Piring | 1 | 1 | 4 | 4 |  | 4 | 2 | 2 |  | 2
| 6 | Peturasan Katup Gelontor | 1 |  | 5 | 5 |  |  | 5 | 5
| 7 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI 1 |  |  |  |  | 80 | 30 | 18 | TOTAL LANTAI 1 | 78 | 30 | 16
LANTAI 2
| 1 | Kloset Tangki Gelontor | 6 |  | 5 |  | 30 |  | 5 |  | 30
| 2 | Kloset katup Gelontor | 2 |  | 10 | 20 |  |  | 10 | 20
| 3 | Keran | 12 |  | 2 | 24 |  |  | 2 | 24
| 4 | Bak Cuci Tangan | 30 | 30 | 2 | 60 |  | 60 | 2 | 60 |  | 60
| 5 | Bak Cuci Piring | 1 | 1 | 4 | 4 |  | 4 | 2 | 2 |  | 2
| 6 | Peturasan Katup Gelontor | 2 | 2 | 5 | 10 |  | 10 | 5 | 10 |  | 10
| 7 | Sink Lab. | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| TOTAL LANTAI 2 |  |  |  |  | 122 | 30 | 78 | TOTAL LANTAI 2 | 120 | 30 | 76
LANTAI 3
| 1 | Kloset Tangki Gelontor | 6 |  | 5 |  | 30 |  | 5 |  | 30
| 2 | Keran | 8 |  | 2 | 16 |  |  | 2 | 16
| 3 | Bak Cuci Tangan | 2 | 1 | 2 | 4 |  | 2 | 2 | 4 |  | 2
| 4 | Shower | 4 | 4 | 2 | 8 |  | 8 | 2 | 8 |  | 8
| 5 | Sink Kran Klinik | 1 | 1 | 3 | 3 |  | 3 | 3 | 3 |  | 3
| 6 | Scrub | 6 | 6 | 4 | 24 |  | 24 | 4 | 24 |  | 24
| TOTAL LANTAI 3 |  |  |  |  | 55 | 30 | 37 | TOTAL LANTAI 3 | 55 | 30 | 37
LANTAI P4A-P5B
| 1 | Kloset Tangki Gelontor | 1 |  | 5 |  | 5 |  | 5 |  | 5
| 2 | Keran | 3 |  | 2 | 6 |  |  | 2 | 6
| TOTAL LANTAI P4A-P5B |  |  |  |  | 6 | 5 |  | TOTAL LANTAI P4A-P5B | 6 | 5 | 0
LANTAI 4
| 1 | Kloset Tangki Gelontor | 8 |  | 5 |  | 40 |  | 5 |  | 40
| 2 | Keran | 10 |  | 2 | 20 |  |  | 2 | 20
| 3 | Bak Cuci Tangan | 3 | 2 | 2 | 6 |  | 4 | 2 | 6 |  | 4
| 4 | Bak Cuci Piring | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
| 5 | Sink Kran Klinik | 6 | 3 | 3 | 18 |  | 9 | 3 | 18 |  | 9
| 6 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI 4 |  |  |  |  | 49 | 40 | 15 | TOTAL LANTAI 4 | 49 | 40 | 15
LANTAI 5
| 1 | Kloset Tangki Gelontor | 15 |  | 5 |  | 75 |  | 5 |  | 75
| 2 | Keran | 15 |  | 2 | 30 |  |  | 2 | 30
| 3 | Bak Cuci Tangan | 20 | 20 | 2 | 40 |  | 40 | 2 | 40 |  | 40
| 4 | Bak Cuci Piring | 1 | 1 | 2 | 2 |  | 2 | 2 | 2 |  | 2
| 5 | Shower | 10 | 6 | 2 | 20 |  | 12 | 2 | 20 |  | 12
| 6 | Sink Kran Klinik | 1 | 1 | 3 | 3 |  | 3 | 3 | 3 |  | 3
| 7 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI 5 |  |  |  |  | 98 | 75 | 57 | TOTAL LANTAI 5 | 98 | 75 | 57
LANTAI P7A
| 1 | Kloset Tangki Gelontor | 1 |  | 5 |  | 5 |  | 5 |  | 5
| 2 | Keran | 3 |  | 2 | 6 |  |  | 2 | 6
| TOTAL LANTAI P7A |  |  |  |  | 6 | 5 | 0 | TOTAL LANTAI P7A | 6 | 5 | 0
LANTAI 6
| 1 | Kloset Tangki Gelontor | 33 |  | 5 |  | 165 |  | 5 |  | 165
| 2 | Kloset Katup Gelontor | 4 |  | 10 | 40 |  |  | 10 | 40
| 3 | Keran | 46 |  | 2 | 92 |  |  | 2 | 92
| 4 | Bak Cuci Tangan | 38 | 31 | 2 | 76 |  | 62 | 2 | 76 |  | 62
| 5 | Peturasan Katup Gelontor | 3 |  | 5 | 15 |  |  | 5 | 15
| 6 | Bak Cuci Piring | 2 | 2 | 2 | 4 |  | 4 | 2 | 4 |  | 4
| 7 | Shower | 36 | 36 | 2 | 72 |  | 72 | 2 | 72 |  | 72
| 8 | Sink Kran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 9 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI 6 |  |  |  |  | 308 | 165 | 144 | TOTAL LANTAI 6 | 308 | 165 | 144
LANTAI 7
| 1 | Kloset Tangki Gelontor | 38 |  | 5 |  | 190 |  | 5 |  | 190
| 2 | Kloset Katup Gelontor | 3 |  | 10 | 30 |  |  | 10 | 30
| 3 | Keran | 44 |  | 2 | 88 |  |  | 2 | 88
| 4 | Bak Cuci Tangan | 59 | 39 | 2 | 118 |  | 78 | 2 | 118 |  | 78
| 5 | Peturasan Katup Gelontor | 2 |  | 5 | 10 |  |  | 5 | 10
| 6 | Bak Cuci Piring | 3 | 3 | 2 | 6 |  | 6 | 2 | 6 |  | 6
| 7 | Shower | 31 | 31 | 2 | 62 |  | 62 | 2 | 62 |  | 62
| 8 | Sink Kran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 9 | Bak Pel | 2 |  | 3 | 6 |  |  | 3 | 6
| TOTAL LANTAI 7 |  |  |  |  | 326 | 190 | 152 | TOTAL LANTAI 7 | 326 | 190 | 152
LANTAI 8
| 1 | Kloset Tangki Gelontor | 31 |  | 5 |  | 155 |  | 5 |  | 155
| 2 | Kloset Katup Gelontor | 3 |  | 10 | 30 |  |  | 10 | 30
| 3 | Keran | 39 |  | 2 | 78 |  |  | 2 | 78
| 4 | Bak Cuci Tangan | 39 | 32 | 2 | 78 |  | 64 | 2 | 78 |  | 64
| 5 | Peturasan Katup Gelontor | 2 |  | 5 | 10 |  |  | 5 | 10
| 6 | Bak Cuci Piring | 7 | 7 | 2 | 14 |  | 14 | 2 | 14 |  | 14
| 7 | Shower | 24 | 24 | 2 | 48 |  | 48 | 2 | 48 |  | 48
| 8 | Sink Kran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 9 | Bak Pel | 2 |  | 3 | 6 |  |  | 3 | 6
| TOTAL LANTAI 8 |  |  |  |  | 270 | 155 | 132 | TOTAL LANTAI 8 | 270 | 155 | 132
LANTAI 9
| 1 | Kloset Tangki Gelontor | 25 |  | 5 |  | 125 |  | 5 |  | 125
| 2 | Kloset Katup Gelontor | 18 |  | 10 | 180 |  |  | 10 | 180
| 3 | Keran | 30 |  | 2 | 60 |  |  | 2 | 60
| 4 | Bak Cuci Tangan | 24 | 24 | 2 | 48 |  | 48 | 2 | 48 |  | 48
| 5 | Peturasan Katup Gelontor | 3 |  | 5 | 15 |  |  | 5 | 15
| 6 | Bak Cuci Piring | 4 | 4 | 2 | 8 |  | 8 | 2 | 8 |  | 8
| 7 | Shower | 16 | 16 | 2 | 32 |  | 32 | 2 | 32 |  | 32
| 8 | Sink Kran Klinik | 2 | 2 | 3 | 6 |  | 6 | 3 | 6 |  | 6
| 9 | Bak Pel | 2 |  | 3 | 6 |  |  | 3 | 6
| TOTAL LANTAI 9 |  |  |  |  | 355 | 125 | 94 | TOTAL LANTAI 9 | 355 | 125 | 94
LANTAI 10
| 1 | Kloset Tangki Gelontor | 21 |  | 5 |  | 105 |  | 5 |  | 105
| 2 | Keran | 24 |  | 2 | 48 |  |  | 2 | 48
| 3 | Bak Cuci Tangan | 26 | 23 | 2 | 52 |  | 46 | 2 | 52 |  | 46
| 4 | Bak Cuci Piring | 8 | 2 | 2 | 16 |  | 4 | 2 | 16 |  | 4
| 5 | Shower | 19 | 19 | 2 | 38 |  | 38 | 2 | 38 |  | 38
| 6 | Sink Kran Klinik | 18 | 18 | 3 | 54 |  | 54 | 3 | 54 |  | 54
| 7 | Bak Pel | 1 |  | 3 | 3 |  |  | 3 | 3
| TOTAL LANTAI 10 |  |  |  |  | 211 | 105 | 142 | TOTAL LANTAI 10 | 211 | 105 | 142
| TOTAL SISTEM 1 (lt.bs-lt.6) |  |  |  |  | 910 | 515 |  | TOTAL SISTEM 1 (lt.bs-lt.6) | 876 | 515
| TOTAL SISTEM 2 (lt.7-lt.10) |  |  |  |  | 1162 | 575 |  | TOTAL SISTEM 2 (lt.7-lt.10) | 1162 | 575
| TOTAL |  |  |  |  | 2072 | 1090 | 969 | TOTAL | 2038 | 1090 | 935
Catatan :
1) SNI 8153 : 2015 Halaman 30 dan 31 (Tabel 3), dan 33 (Tabel 5)
2) SNI 03-7065-2005 Halaman 7 (Tabel 7)

## UBAP BERSIH GD.E
A. | Unit Beban Alat Plumbing Gedung E |  |  | Proyek |  |  | KP
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling)
LANTAI 1
| 1 | Kloset Tangki Gelontor | 5 | 5 |  | 25 | 5 |  | 25
| 2 | Kran | 5 | 2 | 10 |  | 2 | 10
| 3 | Bak Cuci Tangan | 3 | 2 | 6 |  | 2 | 6
| TOTAL LANTAI 1 |  |  |  | 16 | 25 | TOTAL LANTAI 1 | 16 | 25
LANTAI 2
| 1 | Kloset Tangki Gelontor | 8 | 5 |  | 40 | 5 |  | 40
| 2 | Kran | 9 | 2 | 18 |  | 2 | 18
| 3 | Bak Cuci Tangan | 6 | 2 | 12 |  | 2 | 12
| 4 | Bak Cuci Piring | 2 | 2 | 4 |  | 2 | 4
| 5 | Shower | 3 | 2 | 6 |  | 2 | 6
| TOTAL LANTAI 2 |  |  |  | 40 | 40 | TOTAL LANTAI 2 | 40 | 40
| TOTAL |  |  |  | 56 | 65 | TOTAL | 56 | 65
Catatan :
1) SNI 8153 : 2015 Halaman 30 dan 31 (Tabel 3), dan 33 (Tabel 5)
2) SNI 03-7065-2005 Halaman 7 (Tabel 7)

## UBAP BERSIH GD.F
A. | Unit Beban Alat Plumbing Gedung F |  |  | Proyek |  |  | KP
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling) | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Bersih) | Jumlah UBAP (Air Recycling)
LANTAI 1
| 1 | Kloset Tangki Gelontor | 8 | 5 |  | 40 | 5 |  | 40
| 2 | Keran | 8 | 2 | 16 |  | 2 | 16
| TOTAL LANTAI 1 |  |  |  | 16 | 40 | TOTAL LANTAI 1 | 16 | 40
LANTAI 2
| 1 | Kloset Tangki Gelontor | 2 | 5 |  | 10 | 5 |  | 10
| 2 | Keran | 2 | 2 | 4 |  | 2 | 4
| 3 | Bak Cuci Tangan | 2 | 2 | 4 |  | 2 | 4
| 4 | Bak Cuci Piring | 1 | 2 | 2 |  | 2 | 2
| 5 | Bak Pel | 1 | 3 | 3 |  | 3 | 3
| TOTAL LANTAI 2 |  |  |  | 13 | 10 | TOTAL LANTAI 2 | 13 | 10
| TOTAL |  |  |  | 29 | 50 | TOTAL | 29 | 50
Catatan :
1) SNI 8153 : 2015 Halaman 30 dan 31 (Tabel 3), dan 33 (Tabel 5)
2) SNI 03-7065-2005 Halaman 7 (Tabel 7)

## Kebutuhan Air Bersih
A. Gedung A
UBAP Total | 745 |  | UBAP Sistem 1 lantai 1-3 | 431
| 625 | L/menit |  | 410 | L/menit
| 900 | m3/hari |  | 590.4 | m3/hari
UBAP Recycling | 420 |  | UBAP Sistem 2 lantai 4-6 | 314
| 400 | L/menit |  | 305 | L/menit
| 576 | m3/hari |  | 439.2 | m3/hari
UBAP Air Panas | 345 |  | UBAP Recycle Sistem 1 lantai 1-3 | 210
| 348 | L/menit |  | 260 | L/menit
| 501.12 | m3/hari |  | 374.4 | m3/hari
|  |  | UBAP Recycle Sistem 2 lantai 4-6 | 210
|  |  |  | 260 | L/menit
|  |  |  | 374.4 | m3/hari
Kurva perkiraan beban kebutuhan air untuk UBAP sampai dengan 3000
B. Gedung B
UBAP Total | 1446 |  | UBAP Sistem 1 lantai BS-6 | 461
| 970 | L/menit |  | 450 | L/menit
| 1396.8 | m3/hari |  | 648 | m3/hari
UBAP Recycling | 830 |  | UBAP Sistem 2 lantai 7-10 | 985
| 690 | L/menit |  | 760 | L/menit
| 993.6 | m3/hari |  | 1094.4 | m3/hari
UBAP Air Panas | 759 |  | UBAP Recycle Sistem 1 lantai BS-6 | 235
| 649 | L/menit |  | 215 | L/menit
| 934.56 | m3/hari |  | 309.6 | m3/hari
|  |  | UBAP Recycle Sistem 2 lantai 7-10 | 485
|  |  |  | 450 | L/menit
|  |  |  | 648 | m3/hari
Kurva perkiraan beban kebutuhan air untuk UBAP sampai dengan 3000
C. Gedung C
UBAP Total | 2028 |  | UBAP Sistem 1 lantai BS-6 | 1035
| 1230 | L/menit |  | 830 | L/menit
| 1771.2 | m3/hari |  | 1195.2 | m3/hari
UBAP Recycling | 1100 |  | UBAP Sistem 2 lantai 7-10 | 993
| 850 | L/menit |  | 827 | L/menit
| 1224 | m3/hari |  | 1190.88 | m3/hari
UBAP Air Panas | 1035 |  | UBAP Recycle Sistem 1 lantai BS-6 | 525
| 790 | L/menit |  | 480 | L/menit
| 1137.6 | m3/hari |  | 691.2 | m3/hari
|  |  | UBAP Recycle Sistem 2 lantai 7-10 | 575
|  |  |  | 530 | L/menit
|  |  |  | 763.2 | m3/hari
Kurva perkiraan beban kebutuhan air untuk UBAP sampai dengan 3000
D. Gedung D
UBAP Total | 2038 |  | UBAP Sistem 1 lantai BS-6 | 876
| 1250 | L/menit |  | 705 | L/menit
| 1800 | m3/hari |  | 1015.2 | m3/hari
UBAP Recycling | 1090 |  | UBAP Sistem 2 lantai 7-10 | 1162
| 825 | L/menit |  | 860 | L/menit
| 1188 | m3/hari |  | 1238.4 | m3/hari
UBAP Air Panas | 935 |  | UBAP Recycle Sistem 1 lantai BS-6 | 515
| 750 | L/menit |  | 450 | L/menit
| 1080 | m3/hari |  | 648 | m3/hari
|  |  | UBAP Recycle Sistem 2 lantai 7-10 | 575
|  |  |  | 530 | L/menit
|  |  |  | 763.2 | m3/hari
Kurva perkiraan beban kebutuhan air untuk UBAP sampai dengan 3000
E. Gedung E
UBAP Total | 56
| 115 | L/menit
| 165.6 | m3/hari
UBAP Recycling | 65
| 125 | L/menit
| 180 | m3/hari
Kurva perkiraan beban kebutuhan air untuk UBAP sampai dengan 240
F. Gedung F
UBAP Total | 29
| 65 | L/menit
| 93.6 | m3/hari
UBAP Recycling | 50
| 110 | L/menit
| 158.4 | m3/hari
Kurva perkiraan beban kebutuhan air untuk UBAP sampai dengan 240

## Kebutuhan Air Bersih (BED)
PEMAKAIAN AIR RATA-RATA PERORANG PERHARI
No. | Jenis Gedung | Pemakaian Air rata rata sehari | Jangka waktu Pemakaian rata-rata sehari | Perbandingan Luas lantai efektif/total | Keterangan
|  | (Liter) | (Jam) | (%)
1 | Perumahan Mewah | 250 | 8-10 | 42-45 | Setiap Penghuni
2 | Rumah Biasa | 160-250 | 8-10 | 50-53 | Setiap Penghuni
3 | Apartement | 200-250 | 8-10 | 45-50 | Mewah 250 liter
Menengah 180 liter
Bujangan 120 liter
4 | Asrama | 120 | 8
5 | Rumah Sakit | Mewah >1000 |  |  | (Setiap Tempat Tidur Pasien)
|  | Menengah 500-1000 | 8-10 | 45-48 | Pasien Luar: 8 Liter
|  | Umum 350-500 |  |  | Staff/Pegawai: 120 Liter
Keluarga Pasien : 160 Liter
6 | Sekolah Dasar | 40 | 5 | 58-60 | Guru: 100 Liter
7 | SLTP | 50 | 6 | 58-60 | Guru: 100 Liter
8 | SLTA dan Lebih Tinggi | 80 | 6 | 58-60 | Guru / Dosen: 100 Liter
9 | Rumah Toko | 100-200 | 8
10 | Gedung Kantor | 100 | 8 | 60-70 | Setiap Pegawai
11 | Toserba (Toko Serba ada, Departement Store) | 3 | 7 | 55-60 | Pemakaian air hanya untuk kakus, belum termasuk untuk bagian restoran
12 | Pabrik/Industri | Buruh pria: 60 | 8 |  | Per orang, setiap giliran (kalau kerja lebih dari 8 jam sehari)
Buruh Wanita : 100
13 | Stasiun/Terminal | 3 | 15 |  | Setiap Penumpang (yang tiba maupun berangkat)
14 | Restoran | 30 | 5 |  | Untuk Penghuni: 160 Liter
15 | Restoran Umum | 15 | 7 |  | Untuk Penghuni: 160 Liter , Pelayan; 100 Liter 70% dari Jumlah tamu perlu 15 Liter untuk orang kakus dancuci tangan
16 | Gedung Pertunjukan | 30 | 5 | 53-55 | Kalau digunakan siang dan malam, pemakaian air dihitung per penonton. Jam pemakaian air dalam tabel adalah untuk satukali pertunjukan
17 | Gedung Bioskop | 10 | 3 |  | Kalau digunakan siang dan malam, pemakaian air dihitung per penonton. Jam pemakaian air dalam tabel adalah untuk satukali pertunjukan
18 | Toko Pengecer | 40 | 6 |  | Pedagang besar: 30 Liter/ Tamu
150 Liter/ staff atau 5 Liter perhari setiap m2 luas lantai
19 | Hotel Penginapan | 250-300 | 10 |  | untuk setiap tamu, untuk staff 120-150 Liter, penginapan 200 liter
20 | Gedung Peribadatan | 10 | 2 |  | didasarkan pada jumlah jemaah perhari
21 | Perpustakaan | 25 | 6 |  | untuk setiap pembaca yang tinggal
22 | Bar | 30 | 6 |  | Setiap Tamu
23 | Perkumpulan Sosial | 30 | 6 |  | Setiap Tamu
24 | Club Malam | 120-350 |  |  | Setiap Tempat duduk
25 | Gedung Perkumpulan | 150-200 |  |  | Setiap Tamu
26 | Laboratorium | 100-200 | 8 |  | Setiap Staff
*Sumber: Perancangan dan Pemeliharaan Sistem Plumbing, Soufyan Moh.Noerbambang dan Takeo Momimura
| Qh |  | Qh |  |  | C1 | C2
| [ Qd / T ] |  | [ (Qm-max x 60) / C2 ] |  |  | 2 | 3
| Qm-max |  | Qd | Qs |  | C1 : Rentang 1,5 - 2,0
| [ C2 x (Qh / T ] |  | Qh x T | [ 2/3 x Qh ] atau [ Qd / T ] |  | C2 : Rentang 3,0 - 4,0
| *(Noerbambang & Morimura, 2005) |  |  |  |  | *(Noerbambang & Morimura, 2005)
| Qm-max | 23160 | L/menit |  |  | t | 10
| Qh | 77200 | L/jam |  |  | t : Jangka waktu pemakaian (jam)
| Qd | 772000 | Liter
|  | 772 | m3
| Qs | 51466.6667 | Liter/jam
VR (Volume GWT) Air Bersih
| 257333.3333 | Liter
| 0 | Safety Factor
| 257.3333 | m3/hari
| 2 | Cadangan
| 514.6667 | m3
No. | Jenis Gedung | Pemakaian Air rata rata sehari | Jangka waktu Pemakaian rata-rata sehari | Perbandingan Luas lantai efektif/total | Keterangan
|  | (Liter) | (Jam) | (%)
| Rumah Sakit | Mewah >1000 |  |  | (Setiap Tempat Tidur Pasien)
|  | Menengah 500-1000 | 8-10 | 45-48 | Pasien Luar: 8 Liter
|  | Umum 350-500 |  |  | Staff/Pegawai: 120 Liter
Keluarga Pasien : 160 Liter
*Sumber: Perancangan dan Pemeliharaan Sistem Plumbing, Soufyan Moh.Noerbambang dan Takeo Momimura

## Diameter Pipa Air Bersih
Persamaan Kontinuitas
Q = A.v |  |  | A : | [ (1/4) 𝜋 d² ]
Keterangan : |  |  | v : | Rentang 0,9 m/s - 2,0 m/s
A : Luas penampang (m2) |  |  | d : | [ ]
V : Kecepatan aliran fluida (m/s)
Q = Debit aliran (m3/s)
A. Diameter Pipa Air Bersih Gedung A |  |  |  | E. Diameter Pipa Air Bersih Gedung C |  |  | I. Diameter Pipa Air Bersih Gedung E
Main Pipe |  |  |  | Main Pipe |  |  | Main Pipe
UBAP | 745 |  |  | UBAP | 2028 |  | UBAP | 56
| 625 | L/menit |  |  | 1230 | L/menit |  | 115 | L/menit
| 0.010417 | m3/s |  |  | 0.0205 | m3/s |  | 0.0019167 | m3/s
v | 1.5 | m/s |  | v | 2 | m/s | v | 1.5 | m/s
Diameter Perhitungan | 0.094055 | m |  | Diameter Perhitungan | 0.11427 | m | Diameter Perhitungan | 0.040345 | m
| 94.0554 | mm |  |  | 114.2687 | mm |  | 40.3453 | mm
PVC | 100 | mm |  | PVC | 150 | mm | PVC | 50 | mm
PPR | 110 | mm |  | PPR | 160 | mm | PPR | 63 | mm
Pipa Riser (lt.1 - lt.3) |  |  |  | Pipa Riser (lt.bs - lt.6) |  |  | J. Diameter Pipa Air Recycling Gedung E
UBAP | 431 |  |  | UBAP | 1035
| 410 | L/menit |  |  | 830 | L/menit | Main Pipe
| 0.0068333 | m3/s |  |  | 0.013833 | m3/s | UBAP | 65
v | 1.5 | m/s |  | v | 2 | m/s |  | 125 | L/menit
Diameter Perhitungan | 0.076179 | m |  | Diameter Perhitungan | 0.093867 | m |  | 0.0020833 | m3/s
| 76.1791 | mm |  |  | 93.8671 | mm | v | 1.5 | m/s
PVC | 100 | mm |  | PVC | 100 | mm | Diameter Perhitungan | 0.042063 | m
PPR | 110 | mm |  | PPR | 110 | mm |  | 42.0629 | mm
[7 empty] | PVC | 50 | mm
Pipa Riser (lt.4 - lt.6) |  |  |  | Pipa Riser (lt.7 - lt.10) |  |  | PPR | 63 | mm
UBAP | 314 |  |  | UBAP | 993
| 305 | L/menit |  |  | 827 | L/menit | K. Diameter Pipa Air Bersih Gedung F
| 0.0050833 | m3/s |  |  | 0.013783 | m3/s
v | 1.5 | m/s |  | v | 2 | m/s | Main Pipe
Diameter Perhitungan | 0.065704 | m |  | Diameter Perhitungan | 0.093697 | m | UBAP | 29
| 65.7043 | mm |  |  | 93.6973 | mm |  | 65 | L/menit
PVC | 75 | mm |  | PVC | 100 | mm |  | 0.0010833 | m3/s
PPR | 90 | mm |  | PPR | 110 | mm | v | 1.5 | m/s
[7 empty] | Diameter Perhitungan | 0.030332 | m
B. Diameter Pipa Air Recycle Gedung A |  |  |  | F. Diameter Pipa Air Recycle Gedung C |  |  |  | 30.332 | mm
[7 empty] | PVC | 35 | mm
Main Pipe |  |  |  | Main Pipe |  |  | PPR | 40 | mm
UBAP | 420 |  |  | UBAP | 1100
| 400 | L/menit |  |  | 850 | L/menit | K. Diameter Pipa Air Recycling Gedung F
| 0.0066667 | m3/s |  |  | 0.014167 | m3/s
v | 1.5 | m/s |  | v | 2 | m/s | Main Pipe
Diameter Perhitungan | 0.075244 | m |  | Diameter Perhitungan | 0.094991 | m | UBAP | 50
| 75.2444 | mm |  |  | 94.9913 | mm |  | 110 | L/menit
PVC | 75 | mm |  | PVC | 100 | mm |  | 0.0018333 | m3/s
PPR | 90 | mm |  | PPR | 110 | mm | v | 1.5 | m/s
[7 empty] | Diameter Perhitungan | 0.039458 | m
Pipa Riser (lt.1 - lt.3) |  |  |  | Pipa Riser (lt.bs - lt.6) |  |  |  | 39.4585 | mm
UBAP | 210 |  |  | UBAP | 525 |  | PVC | 40 | mm
| 260 | L/menit |  |  | 480 | L/menit | PPR | 50 | mm
| 0.0043333 | m3/s |  |  | 0.008 | m3/s
v | 1.5 | m/s |  | v | 2 | m/s
Diameter Perhitungan | 0.060664 | m |  | Diameter Perhitungan | 0.071383 | m
| 60.6639 | mm |  |  | 71.3831 | mm
PVC | 65 | mm |  | PVC | 75 | mm
PPR | 75 | mm |  | PPR | 90 | mm
Pipa Riser (lt.4 - lt.6) |  |  |  | Pipa Riser (lt.7 - lt.10)
UBAP | 210 |  |  | UBAP | 575
| 260 | L/menit |  |  | 530 | L/menit
| 0.0043333 | m3/s |  |  | 0.0088333 | m3/s
v | 1.5 | m/s |  | v | 2 | m/s
Diameter Perhitungan | 0.060664 | m |  | Diameter Perhitungan | 0.075009 | m
| 60.6639 | mm |  |  | 75.0088 | mm
PVC | 65 | mm |  | PVC | 75 | mm
PPR | 75 | mm |  | PPR | 90 | mm
C. Diameter Pipa Air Bersih Gedung B |  |  |  | G. Diameter Pipa Air Bersih Gedung D
Main Pipe |  |  |  | Main Pipe
UBAP | 1446 |  |  | UBAP | 2038
| 970 | L/menit |  |  | 1250 | L/menit
| 0.016167 | m3/s |  |  | 0.020833 | m3/s
v | 2 | m/s |  | v | 2 | m/s
Diameter Perhitungan | 0.10148 | m |  | Diameter Perhitungan | 0.11519 | m
| 101.4753 | mm |  |  | 115.1939 | mm
PVC | 100 | mm |  | PVC | 150 | mm
PPR | 110 | mm |  | PPR | 160 | mm
Pipa Riser (lt. BS - lt. 6) |  |  |  | Pipa Riser (lt. bs - lt.6)
UBAP | 461 |  |  | UBAP | 876
| 450 | L/menit |  |  | 705 | L/menit
| 0.0075 | m3/s |  |  | 0.01175 | m3/s
v | 2 | m/s |  | v | 2 | m/s
Diameter Perhitungan | 0.069116 | m |  | Diameter Perhitungan | 0.086511 | m
| 69.1164 | mm |  |  | 86.5106 | mm
PVC | 75 | mm |  | PVC | 100 | mm
PPR | 90 | mm |  | PPR | 110 | mm
Pipa Riser (lt. 7 - lt. 10) |  |  |  | Pipa Riser (lt.7 - lt.10)
UBAP | 985 |  |  | UBAP | 1162
| 760 | L/menit |  |  | 860 | L/menit
| 0.012667 | m3/s |  |  | 0.014333 | m3/s
v | 2 | m/s |  | v | 2 | m/s
Diameter Perhitungan | 0.089822 | m |  | Diameter Perhitungan | 0.095548 | m
| 89.8217 | mm |  |  | 95.5485 | mm
PVC | 100 | mm |  | PVC | 100 | mm
PPR | 110 | mm |  | PPR | 110 | mm
D. Diameter Pipa Air Recycle Gedung B |  |  |  | H. Diameter Pipa Air Recycle Gedung D
Main Pipe |  |  |  | Main Pipe
UBAP | 830 |  |  | UBAP | 1090
| 970 | L/menit |  |  | 825 | L/menit
| 0.016167 | m3/s |  |  | 0.01375 | m3/s
v | 2 | m/s |  | v | 2 | m/s
Diameter Perhitungan | 0.10148 | m |  | Diameter Perhitungan | 0.093584 | m
| 101.4753 | mm |  |  | 93.584 | mm
PVC | 100 | mm |  | PVC | 100 | mm
PPR | 110 | mm |  | PPR | 110 | mm
Pipa Riser (lt. BS - lt. 6) |  |  |  | Pipa Riser (lt. BS - lt.6)
UBAP | 235 |  |  | UBAP | 515
| 215 | L/menit |  |  | 450 | L/menit
| 0.0035833 | m3/s |  |  | 0.0075 | m3/s
v | 2 | m/s |  | v | 2 | m/s
Diameter Perhitungan | 0.047774 | m |  | Diameter Perhitungan | 0.069116 | m
| 47.7742 | mm |  |  | 69.1164 | mm
PVC | 65 | mm |  | PVC | 75 | mm
PPR | 75 | mm |  | PPR | 90 | mm
Pipa Riser (lt. 7 - lt. 10) |  |  |  | Pipa Riser (lt.7 - lt.10)
UBAP | 485 |  |  | UBAP | 575
| 450 | L/menit |  |  | 530 | L/menit
| 0.0075 | m3/s |  |  | 0.0088333 | m3/s
v | 2 | m/s |  | v | 2 | m/s
Diameter Perhitungan | 0.069116 | m |  | Diameter Perhitungan | 0.075009 | m
| 69.1164 | mm |  |  | 75.0088 | mm
PVC | 75 | mm |  | PVC | 75 | mm
PPR | 90 | mm |  | PPR | 90 | mm
Air Bersih |  | Air Recycling
Pipa | Diameter (mm) | Pipa | Diameter (mm)
Main Gedung A | 100 | Main Gedung A | 75
Riser 1 Gedung A | 100 | Riser 1 Gedung A | 65
Riser 2 Gedung A | 75 | Riser 2 Gedung A | 65
Main Gedung B | 100 | Main Gedung B | 100
Riser 1 Gedung B | 75 | Riser 1 Gedung B | 65
Riser 2 Gedung B | 100 | Riser 2 Gedung B | 75
Main Gedung C | 150 | Main Gedung C | 100
Riser 1 Gedung C | 100 | Riser 1 Gedung C | 75
Riser 2 Gedung C | 100 | Riser 2 Gedung C | 75
Main Gedung D | 150 | Main Gedung D | 100
Riser 1 Gedung D | 100 | Riser 1 Gedung D | 75
Riser 2 Gedung D | 100 | Riser 2 Gedung D | 75
Main Gedung E | 50 | Main Gedung E | 50
Main Gedung F | 35 | Main Gedung F | 40
𝜋
〖((𝑄.4)/(𝑣.3,14)〗^(1/2)

## Volume GWT
Metode UBAP
Volume GWT
[ Qd - ( Qs x t) ] x T
*(Noerbambang & Morimura, 2005)
Keterangan
Qd | Jumlah kebutuhan air per hari (m3/hari)
Qs | Kapasitas pipa dinas (m3/jam)
t | Pemakaian air 1 hari (jam/hari)
T | Waktu penampungan (hari)
Gedung | UBAP Air Bersih | UBAP Air Panas | Kebutuhan Air (Air Bersih) L/menit
A | 745 | 345 | 625
B | 1446 | 759 | 970
C | 2028 | 1035 | 1230
D | 2038 | 935 | 1250
E | 56 |  | 115
F | 29 |  | 65
Total |  |  | 4255
Qh |  | Qh |  | C1 | C2
[ Qd / T ] |  | [ (Qm-max x 60) / C2 ] |  | 2 | 3
Qm-max |  | Qd | Qs | C1 : Rentang 1,5 - 2,0
[ C2 x (Qh / T ] |  | Qh x T | [ 2/3 x Qh ] atau [ Qd / T ] | C2 : Rentang 3,0 - 4,0
*(Noerbambang & Morimura, 2005)
*(Noerbambang & Morimura, 2005) |  |  |  | *(Noerbambang & Morimura, 2005)
[6 empty] | A |  |  | B |  |  | E
[6 empty] | Qm-max | 625 | L/menit | Qm-max | 970 | L/menit | Qm-max | 115 | L/menit
Qm-max | 4255 | L/menit |  | t | 10 | Qh | 12500 | L/jam | Qh | 19400 | L/jam | Qh | 2300 | L/jam
Qh | 85100 | L/jam |  | t : Jangka waktu pemakaian (jam) |  | Qd | 125000 | Liter | Qd | 194000 | Liter | Qd | 23000 | Liter
Qd | 851000 | Liter |  |  |  |  | 125 | m3 |  | 194 | m3 |  | 23 | m3
| 851 | m3 |  |  |  | Qs | 8333.3333 | Liter/jam | Qs | 12933.3333 | Liter/jam | Qs | 1533.3333 | Liter/jam
Qs | 56733.3333 | Liter/jam
[6 empty] | VR (Volume GWT) Air Bersih |  |  | VR (Volume GWT) Air Bersih |  |  | VR (Volume GWT) Air Bersih
VR (Volume GWT) Air Bersih | [5 empty] | 41666.6667 | Liter |  | 64666.6667 | Liter |  | 7666.6667 | Liter
283666.6667 | Liter |  |  |  |  | 0 | Safety Factor |  | 0 | Safety Factor |  | 0 | Safety Factor
0 | Safety Factor |  |  |  |  | 41.6667 | m3/hari |  | 64.6667 | m3/hari |  | 7.6667 | m3/hari
283.6667 | m3/hari |  |  |  |  | 2 | Cadangan (hari) |  | 2 | Cadangan (hari) |  | 2 | Cadangan (hari)
2 | Cadangan (hari) |  |  |  |  | 83.3333 | m3 |  | 129.3333 | m3 |  | 15.3333 | m3
567.3333 | m3 | 600
[6 empty] | C |  |  | D |  |  | F
Gedung | UBAP Air Recycling | Kebutuhan Air (Air Recycling) L/menit |  |  |  | Qm-max | 1230 | L/menit | Qm-max | 1250 | L/menit | Qm-max | 65 | L/menit
[6 empty] | Qh | 24600 | L/jam | Qh | 25000 | L/jam | Qh | 1300 | L/jam
A | 420 | 400 |  |  |  | Qd | 246000 | Liter | Qd | 250000 | Liter | Qd | 13000 | Liter
B | 830 | 690 |  |  |  |  | 246 | m3 |  | 250 | m3 |  | 13 | m3
C | 1100 | 850 |  |  |  | Qs | 16400 | Liter/jam | Qs | 16666.6667 | Liter/jam | Qs | 866.6667 | Liter/jam
D | 1090 | 825
E | 65 | 125 |  |  |  | VR (Volume GWT) Air Bersih |  |  | VR (Volume GWT) Air Bersih |  |  | VR (Volume GWT) Air Bersih
F | 50 | 110 |  |  |  | 82000 | Liter |  | 83333.3333 | Liter |  | 4333.3333 | Liter
Total | 3555 | 3000 |  |  |  | 0 | Safety Factor |  | 0 | Safety Factor |  | 0 | Safety Factor
[6 empty] | 82 | m3/hari |  | 83.3333 | m3/hari |  | 4.3333 | m3/hari
Qm-max | 3000 | L/menit |  |  |  | 2 | Cadangan (hari) |  | 2 | Cadangan (hari) |  | 2 | Cadangan (hari)
Qh | 60000 | L/jam |  |  |  | 164 | m3 |  | 166.6667 | m3 |  | 8.6667 | m3
Qd | 600000 | Liter
| 600 | m3 |  |  |  | 567.3333
Qs | 40000 | Liter
VR (Volume GWT) Air Recycling | [5 empty] | A |  |  | B |  |  | E
200000 | Liter |  |  |  |  | Qm-max | 400 | L/menit | Qm-max | 690 | L/menit | Qm-max | 125 | L/menit
0 | Safety Factor |  |  |  |  | Qh | 8000 | L/jam | Qh | 13800 | L/jam | Qh | 2500 | L/jam
200 | m3/hari |  |  |  |  | Qd | 80000 | Liter | Qd | 138000 | Liter | Qd | 25000 | Liter
2 | Cadangan (hari) | [5 empty] | 80 | m3 |  | 138 | m3 |  | 25 | m3
400 | m3 |  |  |  |  | Qs | 5333.3333 | Liter/jam | Qs | 9200 | Liter/jam | Qs | 1666.6667 | Liter/jam
[6 empty] | VR (Volume GWT) Air Bersih |  |  | VR (Volume GWT) Air Bersih |  |  | VR (Volume GWT) Air Bersih
[6 empty] | 26666.6667 | Liter |  | 46000 | Liter |  | 8333.3333 | Liter
[6 empty] | 0 | Safety Factor |  | 0 | Safety Factor |  | 0 | Safety Factor
[6 empty] | 26.6667 | m3/hari |  | 46 | m3/hari |  | 8.3333 | m3/hari
[6 empty] | 2 | Cadangan (hari) |  | 2 | Cadangan (hari) |  | 2 | Cadangan (hari)
[6 empty] | 53.3333 | m3 |  | 92 | m3 |  | 16.6667 | m3
[6 empty] | C |  |  | D |  |  | F
[6 empty] | Qm-max | 850 | L/menit | Qm-max | 825 | L/menit | Qm-max | 110 | L/menit
[6 empty] | Qh | 17000 | L/jam | Qh | 16500 | L/jam | Qh | 2200 | L/jam
[6 empty] | Qd | 170000 | Liter | Qd | 165000 | Liter | Qd | 22000 | Liter
[7 empty] | 170 | m3 |  | 165 | m3 |  | 22 | m3
[6 empty] | Qs | 11333.3333 | Liter/jam | Qs | 11000 | Liter/jam | Qs | 1466.6667 | Liter/jam
[6 empty] | VR (Volume GWT) Air Bersih |  |  | VR (Volume GWT) Air Bersih |  |  | VR (Volume GWT) Air Bersih
[6 empty] | 56666.6667 | Liter |  | 55000 | Liter |  | 7333.3333 | Liter
[6 empty] | 0 | Safety Factor |  | 0 | Safety Factor |  | 0 | Safety Factor
[6 empty] | 56.6667 | m3/hari |  | 55 | m3/hari |  | 7.3333 | m3/hari
[6 empty] | 2 | Cadangan (hari) |  | 2 | Cadangan (hari) |  | 2 | Cadangan (hari)
[6 empty] | 113.3333 | m3 |  | 110 | m3 |  | 14.6667 | m3

## Volume RT
A. Air Bersih
Volume Roof Tank | [6 empty] | Detail :
[ (Qp - Qmax) Tp + Qpu x Tpu ] | [6 empty] | Gedung A dan E dari gedung D
Gedung F dari gedung B
*(Noerbambang & Morimura, 2005)
Keterangan : | [6 empty] | C1 | C2
Qp | Kebutuhan puncak (liter/menit) | [5 empty] | 2 | 3.5
Qmax | Kebutuhan jam puncak (liter/menit)
Tp | Jangka waktu kebutuhan puncak (menit) | [5 empty] | C1 : Rentang 1,5 - 2,0
Qpu | Kapasitas pompa pengisi (liter/menit) | [5 empty] | C2 : Rentang 3,0 - 4,0
Tpu | Jangka waktu kerja pompa pengisi (menit)
*(Noerbambang & Morimura, 2005)
Gedung | UBAP Air Bersih | UBAP Air Panas | Kebutuhan Air (Air Bersih) L/menit
[7 empty] | Tpu | Asumsi
A | 745 | 345 | 625 |  |  |  | Tp | Asumsi
B | 1446 | 759 | 970
C | 2028 | 1035 | 1230
D | 2038 | 935 | 1250
E | 56 |  | 115
F | 29 |  | 65
Total |  |  | 4255
| RT 1 (B) | RT 2 (C) | RT 3 (D)
Air Bersih | 1035 | 1230 | 1990
RT 1 (B) |  |  |  | RT 2 (C) |  |  |  | RT 3 (D)
Qm-max | 1035 | L/menit |  | Qm-max | 1230 | L/menit |  | Qm-max | 1990 | L/menit
| 1.035 | m3/menit |  |  | 1.23 | m3/menit |  |  | 1.99 | m3/menit
Qh | 17.7429 | m3/jam |  | Qh | 21.0857 | m3/jam |  | Qh | 34.1143 | m3/jam
Qh-max | 35.4857 | m3/jam |  | Qh-max | 42.1714 | m3/jam |  | Qh-max | 68.2286 | m3/jam
Qp = Qm- max | 1.035 | m3/menit |  | Qp = Qm- max | 1.23 | m3/menit |  | Qp = Qm- max | 1.99 | m3/menit
Qmax | 0.59143 | m3/menit |  | Qmax | 0.70286 | m3/menit |  | Qmax | 1.1371 | m3/menit
Tp | 30 | menit |  | Tp | 30 | menit |  | Tp | 30 | menit
Tpu | 10 | menit |  | Tpu | 10 | menit |  | Tpu | 10 | menit
Qpu | 0.59143 | m3/menit |  | Qpu | 0.70286 | m3/menit |  | Qpu | 1.1371 | m3/menit
VE | 20 | m3 |  | VE | 23 | m3 |  | VE | 37 | m3
Qh | Qh
[ Qd / T ] | [ (Qm-max x 60) / C2 ]
B. Air Recycling
Gedung | UBAP Air Recycling | Kebutuhan Air (Air Recyling) L/menit
A | 420 | 400
B | 830 | 690
C | 1100 | 850
D | 1090 | 825
E | 65 | 125
F | 50 | 110
Total |  | 3000
| RT 1 (B) | RT 2 (C) | RT 3 (D)
Air Recycling | 800 | 850 | 1350
RT 1 (B) |  |  |  | RT 2 (C) |  |  |  | RT 3 (D)
Qm-max | 800 | L/menit |  | Qm-max | 850 | L/menit |  | Qm-max | 1350 | L/menit
| 0.8 | m3/menit |  |  | 0.85 | m3/menit |  |  | 1.35 | m3/menit
Qh | 13.7143 | m3/jam |  | Qh | 14.5714 | m3/jam |  | Qh | 23.1429 | m3/jam
Qh-max | 27.4286 | m3/jam |  | Qh-max | 29.1429 | m3/jam |  | Qh-max | 46.2857 | m3/jam
Qp = Qm- max | 0.8 | m3/menit |  | Qp = Qm- max | 0.85 | m3/menit |  | Qp = Qm- max | 1.35 | m3/menit
Qmax | 0.45714 | m3/menit |  | Qmax | 0.48571 | m3/menit |  | Qmax | 0.77143 | m3/menit
Tp | 30 | menit |  | Tp | 30 | menit |  | Tp | 30 | menit
Tpu | 10 | menit |  | Tpu | 10 | menit |  | Tpu | 10 | menit
Qpu | 0.45714 | m3/menit |  | Qpu | 0.48571 | m3/menit |  | Qpu | 0.77143 | m3/menit
VE | 15 | m3 |  | VE | 16 | m3 |  | VE | 26 | m3
[ (Qp - Qmax) Tp + Qpu x Tpu ]
Qp = Qm- max
qpu = qmax
Air Bersih |  | Air Recycling
Roof Tank | Kapasitas (m3) | Roof Tank | Kapasitas (m3)
Roof Tank 1 | 20 | Roof Tank 1 | 15
Roof Tank 2 | 23 | Roof Tank 2 | 16
Roof Tank 3 | 37 | Roof Tank 3 | 26

## Pompa Transfer
Kapasitas Pompa Transfer Air Bersih
Detail :
UBAP Gedung A | 625 | L/Menit |  |  |  |  | Gedung A dan E dari gedung D
UBAP Gedung B | 970 | L/Menit |  |  |  |  | Gedung F dari gedung B
UBAP Gedung C | 1230 | L/Menit
UBAP Gedung D | 1250 | L/Menit
UBAP Gedung E | 115 | L/Menit
UBAP Gedung F | 65 | L/Menit
AIR BERSIH
A. Pompa Transfer Gedung B |  |  |  | B. Pompa Transfer Gedung C |  |  |  | C. Pompa Transfer Gedung D
Q | 1035 | L/min |  | Q | 1230 | L/min |  | Q | 1990 | L/min
| 0.01725 | m3/s |  |  | 0.0205 | m3/s |  |  | 0.033167 | m3/s
v | 2 | m/s |  | v | 2 | m/s |  | v | 2 | m/s
D | 0.10482 | m |  | D | 0.11427 | m |  | D | 0.14535 | m
| 104.8201 | mm |  |  | 114.2687 | mm |  |  | 145.3453 | mm
PVC | 150 | mm |  | PVC | 150 | mm |  | PVC | 150 | mm
PPR | 160 | mm |  | PPR | 160 | mm |  | PPR | 160 | mm
Friction Head Loss |  |  |  | Friction Head Loss |  |  |  | Friction Head Loss
Major Head Loss |  |  |  | Major Head Loss |  |  |  | Major Head Loss
Q | 0.01725 |  | m3/s | Q | 0.0205 |  | m3/s | Q | 0.033167 |  | m3/s
C | 150 |  |  | C | 150 |  |  | C | 150
D | 0.10482 |  | m | D | 0.11427 |  | m | D | 0.14535 |  | m
L | 98.355 |  | m | L | 93.889 |  | m | L | 132.543 |  | m
hf | 3.1892 |  | m | hf | 2.752 |  | m | hf | 2.932 |  | m
Minor Head Loss |  |  |  | Minor Head Loss |  |  |  | Minor Head Loss
Fitting | Jumlah | k | K total | Fitting | Jumlah | k | K total | Fitting | Jumlah | k | K total
Elbow 90 | 7 | 0.7 | 4.9 | Elbow 90 | 7 | 0.7 | 4.9 | Elbow 90 | 7 | 0.7 | 4.9
Tees Line Flow | 1 | 0.2 | 0.2 | Tees Line Flow | 1 | 0.2 | 0.2 | Tees Line Flow | 1 | 0.2 | 0.2
Gate valve | 4 | 0.15 | 0.6 | Gate valve | 4 | 0.15 | 0.6 | Gate valve | 4 | 0.15 | 0.6
Flexible Joint | 2 | 0.04 | 0.08 | Flexible Joint | 2 | 0.04 | 0.08 | Flexible Joint | 2 | 0.04 | 0.08
Strainer | 1 | 1 | 1 | Strainer | 1 | 1 | 1 | Strainer | 1 | 1 | 1
Check Valve | 1 | 2.6 | 2.6 | Check Valve | 1 | 2.6 | 2.6 | Check Valve | 1 | 2.6 | 2.6
K Total |  |  | 9.38 | K Total |  |  | 9.38 | K Total |  |  | 9.38
v | 2 |  | m/s | v | 2 |  | m/s | v | 2 |  | m/s
v2 | 4 |  | m2/s2 | v2 | 4 |  | m2/s2 | v2 | 4 |  | m2/s2
g | 9.81 |  | m/s2 | g | 9.81 |  | m/s2 | g | 9.81 |  | m/s2
2g | 19.62 |  | m/s2 | 2g | 19.62 |  | m/s2 | 2g | 19.62 |  | m/s2
hf | 1.9123 |  | m | hf | 1.9123 |  | m | hf | 1.9123 |  | m
Static Head |  |  |  | Static Head |  |  |  | Static Head
Static Head Loss |  | 53.458 | m | Static Head Loss |  | 54.106 | m | Static Head Loss |  | 54.721 | m
Velocity Head |  |  |  | Velocity Head |  |  |  | Velocity Head
v | 2 | m/s |  | v | 2 | m/s |  | v | 2 | m/s
v2 | 4 | m2/s2 |  | v2 | 4 | m2/s2 |  | v2 | 4 | m2/s2
g | 9.81 | m/s2 |  | g | 9.81 | m/s2 |  | g | 9.81 | m/s2
Velocity Head | 0.20387 | m |  | Velocity Head | 0.20387 | m |  | Velocity Head | 0.20387 | m
Total head | 58.7634 | m |  | Total head | 58.9742 | m |  | Total head | 59.7692 | m
AIR RECYCLING
A. Pompa Transfer Gedung B |  |  |  | B. Pompa Transfer Gedung C |  |  |  | C. Pompa Transfer Gedung D
Q | 800 | L/min |  | Q | 850 | L/min |  | Q | 1350 | L/min
| 0.013333 | m3/s |  |  | 0.014167 | m3/s |  |  | 0.0225 | m3/s
v | 2 | m/s |  | v | 2 | m/s |  | v | 2 | m/s
D | 0.092155 | m |  | D | 0.094991 | m |  | D | 0.11971 | m
| 92.1551 | mm |  |  | 94.9913 | mm |  |  | 119.713 | mm
PVC | 100 | mm |  | PVC | 100 | mm |  | PVC | 150 | mm
PPR | 110 | mm |  | PPR | 110 | mm |  | PPR | 160 | mm
Friction Head Loss |  |  |  | Friction Head Loss |  |  |  | Friction Head Loss
Major Head Loss |  |  |  | Major Head Loss |  |  |  | Major Head Loss
Q | 0.013333 |  | m3/s | Q | 0.014167 |  | m3/s | Q | 0.0225 |  | m3/s
C | 150 |  |  | C | 150 |  |  | C | 150
D | 0.092155 |  | m | D | 0.094991 |  | m | D | 0.11971 |  | m
L | 99.722 |  | m | L | 98.41 |  | m | L | 129.319 |  | m
hf | 3.7594 |  | m | hf | 3.5806 |  | m | hf | 3.5896 |  | m
Minor Head Loss |  |  |  | Minor Head Loss |  |  |  | Minor Head Loss
Fitting | Jumlah | k | K total | Fitting | Jumlah | k | K total | Fitting | Jumlah | k | K total
Elbow 90 | 7 | 0.7 | 4.9 | Elbow 90 | 7 | 0.7 | 4.9 | Elbow 90 | 7 | 0.7 | 4.9
Tees Line Flow | 1 | 0.2 | 0.2 | Tees Line Flow | 1 | 0.2 | 0.2 | Tees Line Flow | 1 | 0.2 | 0.2
Gate valve | 4 | 0.15 | 0.6 | Gate valve | 4 | 0.15 | 0.6 | Gate valve | 4 | 0.15 | 0.6
Flexible Joint | 2 | 0.04 | 0.08 | Flexible Joint | 2 | 0.04 | 0.08 | Flexible Joint | 2 | 0.04 | 0.08
Strainer | 1 | 1 | 1 | Strainer | 1 | 1 | 1 | Strainer | 1 | 1 | 1
Check Valve | 1 | 2.6 | 2.6 | Check Valve | 1 | 2.6 | 2.6 | Check Valve | 1 | 2.6 | 2.6
K Total |  |  | 9.38 | K Total |  |  | 9.38 | K Total |  |  | 9.38
v | 2 |  | m/s | v | 2 |  | m/s | v | 2 |  | m/s
v2 | 4 |  | m2/s2 | v2 | 4 |  | m2/s2 | v2 | 4 |  | m2/s2
g | 9.81 |  | m/s2 | g | 9.81 |  | m/s2 | g | 9.81 |  | m/s2
2g | 19.62 |  | m/s2 | 2g | 19.62 |  | m/s2 | 2g | 19.62 |  | m/s2
hf | 1.9123 |  | m | hf | 1.9123 |  | m | hf | 1.9123 |  | m
Static Head |  |  |  | Static Head |  |  |  | Static Head
Static Head Loss |  | 54.022 | m | Static Head Loss |  | 53.344 | m | Static Head Loss |  | 52.71 | m
Velocity Head |  |  |  | Velocity Head |  |  |  | Velocity Head
v | 2 | m/s |  | v | 2 | m/s |  | v | 2 | m/s
v2 | 4 | m2/s2 |  | v2 | 4 | m2/s2 |  | v2 | 4 | m2/s2
g | 9.81 | m/s2 |  | g | 9.81 | m/s2 |  | g | 9.81 | m/s2
Velocity Head | 0.20387 | m |  | Velocity Head | 0.20387 | m |  | Velocity Head | 0.20387 | m
Total head | 59.8976 | m |  | Total head | 59.0408 | m |  | Total head | 58.4158 | m

## Pompa Booster
Booster Pump |  | Under 1,5 bar |  | Detail :
PRV |  | Over 3 bar |  | Gedung A dan E dari gedung D
Gedung F dari gedung B
AIR BERSIH
A. Gedung B |  |  | B. Gedung C |  |  | C. Gedung D
Sistem 2 (lt.7 -lt.10) |  |  | Sistem 2 (lt.7 -lt.10) |  |  | Sistem 2 (lt.7 -lt.10)
UBAP | 985 |  | UBAP | 993 |  | UBAP | 1162
Q | 760 | L/min | Q | 827 | L/min | Q | 860 | L/min
| 0.012667 | m3/s |  | 0.013783 | m3/s |  | 0.014333 | m3/s
v | 2 | m/s | v | 2 | m/s | v | 2 | m/s
D | 0.089822 | m | D | 0.093697 | m | D | 0.095548 | m
| 89.8217 | mm |  | 93.6973 | mm |  | 95.5485 | mm
PVC | 100 | mm | PVC | 100 | mm | PVC | 100 | mm
PPR | 110 | mm | PPR | 110 | mm | PPR | 110 | mm
Head pompa :
GEDUNG B |  |  | GEDUNG C |  |  | GEDUNG D
Horizontal | 53.3 | m | Horizontal | 53.3 | m | Horizontal | 53.3 | m
Titik keran terjauh | 0.092 | bar | Titik keran terjauh | 0.092 | bar | Titik keran terjauh | 0.092 | bar
Keran terjauh harus 1,5 bar maka perlu head sebesar | 17 | m | Keran terjauh harus 1,5 bar maka perlu head sebesar | 17 | m | Keran terjauh harus 1,5 bar maka perlu head sebesar | 17 | m | 2 | 0.2 | roof |  |  | 17 | 1.7 | roof
AIR RECYCLING | [9 empty] | riser |  | kran terjauh |  |  | riser |  | kran terjauh
[9 empty] | 4.25 | 0.625 |  | 0.092 | 10 | 4.25 | 2.125 |  | 1.592 | 10
A. Gedung B |  |  | B. Gedung C |  |  | C. Gedung D
Sistem 2 (lt.7 -lt.10) |  |  | Sistem 2 (lt.7 -lt.10) |  |  | Sistem 2 (lt.7 -lt.10) |  |  |  | riser |  | kran terjauh |  |  | riser |  | kran terjauh
UBAP | 485 |  | UBAP | 575 |  | UBAP | 575 |  | 4.25 | 1.05 |  | 0.517 | 9 | 4.25 | 2.55 |  | 2.017 | 9
Q | 450 | L/min | Q | 530 | L/min | Q | 530 | L/min
| 0.0075 | m3/s |  | 0.0088333 | m3/s |  | 0.0088333 | m3/s
v | 2 | m/s | v | 2 | m/s | v | 2 | m/s |  | riser |  | kran terjauh |  |  | riser |  | kran terjauh
D | 0.069116 | m | D | 0.075009 | m | D | 0.075009 | m | 4.25 | 1.475 |  | 0.942 | 8 | 4.25 | 2.975 |  | 2.442 | 8
| 69.1164 | mm |  | 75.0088 | mm |  | 75.0088 | mm
PVC | 75 | mm | PVC | 75 | mm | PVC | 75 | mm
PPR | 90 | mm | PPR | 90 | mm | PPR | 90 | mm |  | riser |  | kran terjauh |  |  | riser |  | kran terjauh
[9 empty] | 4.25 | 1.9 |  | 1.367 | 7 | 4.25 | 3.4 |  | 2.867 | 7
Head pompa :
GEDUNG B |  |  | GEDUNG C |  |  | GEDUNG D
Horizontal | 53.3 | m | Horizontal | 53.3 | m | Horizontal | 53.3 | m
Titik keran terjauh | 0.092 | bar | Titik keran terjauh | 0.092 | bar | Titik keran terjauh | 0.092 | bar
Keran terjauh harus 1,5 bar maka perlu head sebesar | 17 | m | Keran terjauh harus 1,5 bar maka perlu head sebesar | 17 | m | Keran terjauh harus 1,5 bar maka perlu head sebesar | 17 | m

## Rekapitulasi
No | Uraian | Proyek | KP | Satuan
A | Sistem Air Bersih
1 | Kebutuhan Air Bersih Gedung A | 700 | 625 | lpm
2 | Kebutuhan Air Bersih Gedung B | 950 | 970 | L/menit
3 | Kebutuhan Air Bersih Gedung C | 1240 | 1230 | L/menit
4 | Kebutuhan Air Bersih Gedung D | 1250 | 1250 | L/menit
5 | Kebutuhan Air Bersih Gedung E | 125 | 115 | L/menit
6 | Kebutuhan Air Bersih Gedung F | 70 | 65 | L/menit
7 | Kebutuhan Air Bersih Total | 4335 | 4255 | L/menit
8 | Volume GWT Air Bersih | 600 | 567.3333 | m3
9 | Volume Rooftank Air Bersih Gedung B | 30 | 20 | m3
10 | Volume Rooftank Air Bersih Gedung C | 30 | 23 | m3
11 | Volume Rooftank Air Bersih Gedung D | 30 | 37 | m3
12 | Pompa Transfer Air Bersih Gedung B | Kap : 960 lpm, Head : 60 m | Kap : 1035 lpm, Head : 59 m | c | 1035 | 59
13 | Pompa Transfer Air Bersih Gedung C | Kap : 1200 lpm, Head : 60 m | Kap : 1230 lpm, Head : 59 m |  | 1230 | 59
14 | Pompa Transfer Air Bersih Gedung D | Kap : 1500Kap lpm, Head : 60 m | Kap : 1990 lpm, Head : 60 m |  | 1990 | 60
15 | Pompa Booster Air Bersih Gedung B | Kap : 700 lpm, Head : 14 m | Kap : 760 lpm, Head : 17 m |  | 760 | 17
16 | Pompa Booster Air Bersih Gedung C | Kap : 750 lpm, Head : 14 m | Kap : 827 lpm, Head : 17 m |  | 827 | 17
17 | Pompa Booster Air Bersih Gedung D | Kap : 850 lpm, Head : 14 m | Kap : 860 lpm, Head : 17 m |  | 860 | 17
B | Sistem Air Recycling
1 | Kebutuhan Air Recycling Gedung A | 300 | 400 | L/menit
2 | Kebutuhan Air Recycling Gedung B | 700 | 690 | L/menit
3 | Kebutuhan Air Recycling Gedung C | 850 | 850 | L/menit
4 | Kebutuhan Air Recycling Gedung D | 850 | 825 | L/menit
5 | Kebutuhan Air Recycling Gedung E | 130 | 125 | L/menit
6 | Kebutuhan Air Recycling Gedung F | 110 | 110 | L/menit
7 | Kebutuhan Air Recycling Total | 2940 | 3000 | L/menit
8 | Volume GWT Air Recycling | 400 | 400 | m3
9 | Volume Rooftank Air Recycling Gedung B | 30 | 15 | m3
10 | Volume Rooftank Air Recycling Gedung C | 30 | 16 | m3
11 | Volume Rooftank Air Recycling Gedung D | 30 | 26 | m3
12 | Pompa Transfer Air Recycling Gedung B |  | Kap : 800 lpm, Head : 60 m |  | 800 | 60
13 | Pompa Transfer Air Recycling Gedung C | Kap : 850 lpm, Head :60 | Kap : 850 lpm, Head : 59 m |  | 850 | 59
14 | Pompa Transfer Air Recycling Gedung D |  | Kap : 1350 lpm, Head : 58 m |  | 1350 | 58
15 | Pompa Booster Air Recycling Gedung B | Kap : 550 lpm, Head :14 | Kap : 450 lpm, Head : 17 m |  | 450 | 17
16 | Pompa Booster Air Recycling Gedung C | Kap : 575 lpm, Head :14 | Kap : 530 lpm, Head : 17 m |  | 530 | 17
17 | Pompa Booster Air Recycling Gedung D | Kap : 875 lpm, Head :14 | Kap : 530 lpm, Head : 17 m |  | 530 | 17
No | Uraian | Proyek | KP
A | Sistem Air Bersih
1 | Pompa Booster Air Bersih Gedung B | Kap : 700 lpm, Head : 14 m | Kap : 760 lpm, Head : 17 m
2 | Pompa Booster Air Bersih Gedung C | Kap : 750 lpm, Head : 14 m | Kap : 827 lpm, Head : 17 m
3 | Pompa Booster Air Bersih Gedung D | Kap : 850 lpm, Head : 14 m | Kap : 860 lpm, Head : 17 m
B | Sistem Air Recycling
1 | Pompa Booster Air Recycling Gedung B | Kap : 550 lpm, Head :14 | Kap : 450 lpm, Head : 17 m
2 | Pompa Booster Air Recycling Gedung C | Kap : 575 lpm, Head :14 | Kap : 530 lpm, Head : 17 m
3 | Pompa Booster Air Recycling Gedung D | Kap : 875 lpm, Head :14 | Kap : 530 lpm, Head : 17 m

## UBAP LIMBAH GD.A
A. | Unit Beban Alat Plumbing Gedung A
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Jumlah Alat Plumbing AP | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Limbah) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas)
LANTAI 1
| 1 | Kloset Tangki Gelontor | 8 |  | 4 | 32
| 2 | Keran | 8 |  | 2 | 16
| 3 | Bak Cuci Tangan | 21 | 20 | 1 | 21
| 4 | Bak Cuci Piring | 2 | 2 | 2 | 4
| 5 | Shower | 2 | 2 | 2 | 4
| 6 | Sink Kran Klinik | 4 | 4 | 6 | 24
| 7 | Scrub | 6 | 6 | 3 | 18
| 8 | Bak Pel | 1 |  | 3 | 3
| 9 | Sink Lab | 2 | 2 | 3 | 6
| TOTAL LANTAI 1 |  |  |  |  | 128 | 0
LANTAI 2
| 1 | Kloset Tangki Gelontor | 13 |  | 4 | 52
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 16
| 3 | Keran | 15 |  | 2 | 30
| 4 | Bak Cuci Tangan | 14 | 14 | 1 | 14
| 5 | Peturasan Katup Gelontor | 3 |  | 4 | 12
| 6 | Bak Cuci Piring | 2 | 2 | 2 | 4
| 7 | Shower | 3 | 3 | 2 | 6
| 8 | Sink Kran Klinik | 1 | 1 | 6 | 6
| 9 | Scrub | 1 | 1 | 3 | 3
| 10 | Sink Lab | 15 | 15 | 3 | 45
| 11 | Sink Cuci Muka | 1 | 1 | 1 | 1
| TOTAL LANTAI 2 |  |  |  |  | 189 | 0
LANTAI 3
| 1 | Kloset Tangki Gelontor | 21 |  | 4 | 84
| 2 | Keran | 21 |  | 2 | 42
| 3 | Bak Cuci Tangan | 52 | 35 | 1 | 52
| 4 | Peturasan Katup Gelontor | 4 |  | 4 | 16
| 5 | Shower | 4 | 2 | 2 | 8
| 6 | Sink Kran Klinik | 2 | 2 | 6 | 12
| TOTAL LANTAI 3 |  |  |  |  | 214 | 0
LANTAI 4
| 1 | Kloset Tangki Gelontor | 14 |  | 4 | 56
| 2 | Keran | 14 |  | 2 | 28
| 3 | Bak Cuci Tangan | 61 | 38 | 1 | 61
| 4 | Peturasan Katup Gelontor | 4 |  | 4 | 16
| 5 | Sink Kran Klinik | 2 | 2 | 6 | 12
| TOTAL LANTAI 4 |  |  |  |  | 173 | 0
LANTAI 5
| 1 | Kloset Tangki Gelontor | 14 |  | 4 | 56
| 2 | Keran | 14 |  | 2 | 28
| 3 | Bak Cuci Tangan | 8 | 2 | 1 | 8
| 4 | Peturasan Katup Gelontor | 4 |  | 4 | 16
| 5 | Bak Cuci Piring | 2 | 2 | 2 | 4
| TOTAL LANTAI 5 |  |  |  |  | 112 | 0
LANTAI 6
| 1 | Kloset Tangki Gelontor | 14 |  | 4 | 56
| 2 | Keran | 14 |  | 2 | 28
| 3 | Bak Cuci Tangan | 8 | 2 | 1 | 8
| 4 | Peturasan Katup Gelontor | 4 |  | 4 | 16
| 5 | Sink Kran Klinik | 2 | 2 | 6 | 12
| TOTAL LANTAI 6 |  |  |  |  | 120 | 0
| TOTAL SISTEM 1 (lt. 1 - lt 3) |  |  |  |  | 531 | 0
| TOTAL SISTEM 2 (lt. 4 - lt 6) |  |  |  |  | 405 | 0
| TOTAL |  |  |  |  | 936 | 0
Catatan :
| 1) SNI 8153:2015 Halaman 54 |  |  |  |  | 2) SNI 03-7065-2005 Halaman 11 dan 12

## UBAP LIMBAH GD.B
A. | Unit Beban Alat Plumbing Gedung B
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Jumlah Alat Plumbing AP | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Limbah) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas)
LANTAI BASEMENT
| 1 | Kloset Tangki Gelontor | 8 |  | 4 | 32
| 2 | Keran | 8 |  | 2 | 16
| 3 | Bak Cuci Tangan | 5 | 2 | 1 | 5
| 4 | Shower | 8 | 8 | 2 | 16
| TOTAL LANTAI BASEMENT |  |  |  |  | 69 | 0
LANTAI 1
| 1 | Kloset Tangki Gelontor | 6 |  | 4 | 24
| 2 | Keran | 12 |  | 2 | 24
| 3 | Bak Cuci Tangan | 9 | 5 | 1 | 9
| 4 | Peturasan katup Gelontor | 1 |  | 4 | 4
| 5 | Bak Cuci Piring | 2 | 2 | 2 | 4
| 6 | Kloset katup Gelontor | 2 |  | 8 | 16
| TOTAL LANTAI 1 |  |  |  |  | 81 | 0
LANTAI 2
| 1 | Kloset Tangki Gelontor | 5 |  | 4 | 20
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 16
| 3 | Keran | 11 |  | 2 | 22
| 4 | Bak Cuci Tangan | 30 | 30 | 1 | 30
| 5 | Peturasan katup Gelontor | 2 | 2 | 4 | 8
| 6 | Sink Keran Klinik | 2 | 2 | 6 | 12
| TOTAL LANTAI 2 |  |  |  |  | 108 | 0
LANTAI PARKIR P2A-P3B
| 1 | Kloset Tangki Gelontor | 1 |  | 4 | 4
| 2 | Keran | 3 |  | 2 | 6
| TOTAL LANTAI PARKIR P2A-P3B |  |  |  |  | 10 | 0
LANTAI 3
| 1 | Kloset Tangki Gelontor | 5 |  | 4 | 20
| 2 | Keran | 5 |  | 2 | 10
| 3 | Bak Cuci Tangan | 2 | 1 | 1 | 2
| 4 | Scrub | 6 | 6 | 3 | 18
| 5 | Sink keran Klinik/sphk | 1 |  | 6 | 6
| 6 | Shower | 4 | 4 | 2 | 8
| TOTAL LANTAI 3 |  |  |  |  | 64 | 0
LANTAI PARKIR P3A-P4B
| 1 | Kloset Tangki Gelontor | 1 |  | 4 | 4
| 2 | Keran | 3 |  | 2 | 6
| TOTAL LANTAI PARKIR P3A-P4B |  |  |  |  | 10 | 0
LANTAI 4
| 1 | Kloset Tangki Gelontor | 5 |  | 4 | 20
| 2 | Keran | 5 |  | 2 | 10
| 3 | Bak Cuci Tangan | 2 | 1 | 1 | 2
| 4 | Sink keran Klinik/sphk | 2 | 2 | 6 | 12
| 5 | Shower | 4 | 4 | 2 | 8
| TOTAL LANTAI 4 |  |  |  |  | 52 | 0
LANTAI PARKIR P5A-P6B
| 1 | Kloset Tangki Gelontor | 1 |  | 4 | 4
| 2 | Keran | 3 |  | 2 | 6
| TOTAL LANTAI PARKIR P5A-P6B |  |  |  |  | 10 | 0
LANTAI 5
| 1 | Kloset Tangki Gelontor | 5 |  | 4 | 20
| 2 | Keran | 5 |  | 2 | 10
| 3 | Bak Cuci Tangan | 5 | 4 | 1 | 5
| 4 | Sink keran Klinik/sphk | 7 | 3 | 6 | 42
| TOTAL LANTAI 5 |  |  |  |  | 77 | 0
LANTAI PARKIR P6B-P7B
| 1 | Kloset Tangki Gelontor | 1 |  | 4 | 4
| 2 | Keran | 3 |  | 2 | 6
| TOTAL LANTAI PARKIR P6B-P7B |  |  |  |  | 10 | 0
LANTAI 6
| 1 | Kloset Tangki Gelontor | 9 |  | 4 | 36
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 16
| 3 | Keran | 15 |  | 2 | 30
| 4 | Peturasan Katup Gelontor | 1 |  | 4 | 4
| 5 | Bak Cuci Tangan | 12 | 10 | 1 | 12
| 6 | Bak Pel | 1 |  | 3 | 3
| 7 | Bak cuci Piring | 1 | 1 | 2 | 2
| 8 | Shower | 2 | 10 | 2 | 4
| TOTAL LANTAI 6 |  |  |  |  | 107 | 0
LANTAI 7
| 1 | Kloset Tangki Gelontor | 22 |  | 4 | 88
| 2 | Keran | 25 |  | 2 | 50
| 3 | Bak Cuci Tangan | 29 | 25 | 1 | 29
| 4 | Bak Pel | 1 |  | 3 | 3
| 5 | Sink keran Klinik/sphk | 2 | 2 | 6 | 12
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4
| 7 | Shower | 20 | 20 | 2 | 40
| TOTAL LANTAI 7 |  |  |  |  | 226 | 0
LANTAI 7 B1 - LANTAI 9 B2
| 1 | Kloset Tangki Gelontor | 20 |  | 4 | 80
| 2 | Kloset Katup Gelontor | 3 |  | 8 | 24
| 3 | Keran | 23 |  | 2 | 46
| 4 | Bak Cuci Tangan | 19 | 18 | 1 | 19
| 5 | Bak Pel | 1 |  | 3 | 3
| 6 | Bak cuci Piring | 1 | 1 | 2 | 2
| 7 | Shower | 15 | 15 | 2 | 30
| TOTAL LANTAI 7 B1 - LANTAI 9 B2 |  |  |  |  | 204 | 0
LANTAI 8
| 1 | Kloset Tangki Gelontor | 18 |  | 4 | 72
| 2 | Keran | 21 |  | 2 | 42
| 3 | Bak Cuci Tangan | 22 | 21 | 1 | 22
| 4 | Bak Pel | 1 |  | 3 | 3
| 5 | Sink keran Klinik/sphk | 2 | 2 | 6 | 12
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4
| 7 | Shower | 16 | 16 | 2 | 32
| TOTAL LANTAI 8 |  |  |  |  | 187 | 0
LANTAI 8 B1 - LANTAI 10 B2
| 1 | Kloset Tangki Gelontor | 13 |  | 4 | 52
| 2 | Kloset Katup Gelontor | 3 |  | 8 | 24
| 3 | Keran | 27 |  | 2 | 54
| 4 | Bak Cuci Tangan | 15 | 15 | 1 | 15
| 5 | Bak Pel | 1 |  | 3 | 3
| 6 | Bak cuci Piring | 5 | 5 | 2 | 10
| 7 | Shower | 2 | 8 | 2 | 4
| TOTAL LANTAI 8 B1 - LANTAI 10 B2 |  |  |  |  | 162 | 0
LANTAI 9
| 1 | Kloset Tangki Gelontor | 18 |  | 4 | 72
| 2 | Keran | 21 |  | 2 | 42
| 3 | Bak Cuci Tangan | 22 | 21 | 1 | 22
| 4 | Bak Pel | 1 |  | 3 | 3
| 5 | Sink keran Klinik/sphk | 2 | 2 | 6 | 12
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4
| 7 | Shower | 16 | 16 | 2 | 32
| TOTAL LANTAI 9 |  |  |  |  | 187 | 0
LANTAI 9 B1 - LANTAI 11 B2
| 1 | Kloset Tangki Gelontor | 7 |  | 4 | 28
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 16
| 3 | Keran | 9 |  | 2 | 18
| 4 | Bak Cuci Tangan | 5 | 1 | 1 | 5
| 5 | Peturasan katup Gelontor | 3 |  | 4 | 12
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4
| TOTAL LANTAI 9 B1 - LANTAI 11 B2 |  |  |  |  | 83 | 0
LANTAI 10
| 1 | Kloset Tangki Gelontor | 21 |  | 4 | 84
| 2 | Keran | 24 |  | 2 | 48
| 3 | Bak Cuci Tangan | 34 | 23 | 1 | 34
| 4 | Bak Pel | 1 |  | 3 | 3
| 5 | Sink keran Klinik/sphk | 18 | 18 | 6 | 108
| 6 | Bak cuci Piring | 2 | 2 | 2 | 4
| 7 | Shower | 19 | 19 | 2 | 38
| TOTAL LANTAI 10 |  |  |  |  | 319 | 0
| TOTAL SISTEM 1 (lt.bs-lt.6) |  |  |  |  | 598 | 0
| TOTAL SISTEM 2 (lt.7-lt.10) |  |  |  |  | 1142 | 0
| TOTAL |  |  |  |  | 1966 | 0
Catatan :
| 1) SNI 8153:2015 Halaman 54 |  |  |  |  | 2) SNI 03-7065-2005 Halaman 11 dan 12
Note on D23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dari 18
Note on D132: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dari 2
Note on D133: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dari 1

## UBAP LIMBAH GD.C
A. | Unit Beban Alat Plumbing Gedung C
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Jumlah Alat Plumbing AP | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Limbah) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas)
LANTAI BASEMENT
| 1 | Kloset Tangki Gelontor | 13 |  | 4 | 52
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 20
| 3 | Keran | 19 |  | 2 | 38
| 4 | Bak Cuci Tangan | 12 | 11 | 1 | 24
| 5 | Peturasan Katup Gelontor | 2 |  | 4 | 10
| 6 | Sink Kran Klinik | 6 | 5 | 6 | 18
| 7 | Bak Pel | 1 |  | 3 | 3
| 8 | Shower | 6 | 6 | 2 | 12
| TOTAL LANTAI BASEMENT |  |  |  |  | 177 | 0
LANTAI 1
| 1 | Kloset Tangki Gelontor | 5 |  | 4 | 20
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 20
| 3 | Keran | 11 |  | 2 | 22
| 4 | Bak Cuci Tangan | 6 | 2 | 1 | 12
| 5 | Peturasan Katup Gelontor | 1 |  | 4 | 5
| 6 | Bak Cuci Piring | 1 | 1 | 2 | 2
| 7 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI 1 |  |  |  |  | 84 | 0
LANTAI P1A-P2B
| 1 | Kloset Tangki Gelontor | 1 |  | 4 | 4
| 2 | Keran | 3 |  | 2 | 6
| TOTAL LANTAI P1A-P2B |  |  |  |  | 10 | 0
LANTAI 2
| 1 | Kloset Tangki Gelontor | 13 |  | 4 | 52
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 20
| 3 | Keran | 15 |  | 2 | 30
| 4 | Bak Cuci Tangan | 32 | 29 | 1 | 64
| 5 | Peturasan Katup Gelontor | 2 | 2 | 4 | 10
| 6 | Bak Cuci Piring | 1 | 1 | 2 | 2
| 7 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI 2 |  |  |  |  | 181 | 0
LANTAI 3
| 1 | Kloset Tangki Gelontor | 7 |  | 4 | 28
| 2 | Keran | 9 |  | 2 | 18
| 3 | Bak Cuci Tangan | 1 | 1 | 1 | 2
| 4 | Shower | 3 | 3 | 2 | 6
| 5 | Sink Kran Klinik | 2 | 2 | 6 | 6
| 6 | Scrub | 10 | 10 | 3 | 40
| TOTAL LANTAI 3 |  |  |  |  | 100 | 0
LANTAI P4A-P5B
| 1 | Kloset Tangki Gelontor | 2 |  | 4 | 8
| 2 | Keran | 2 |  | 2 | 4
| 3 | Bak Cuci Tangan | 3 | 3 | 1 | 6
| 4 | Bak Cuci Piring | 1 | 1 | 2 | 2
| 5 | Shower | 2 | 2 | 2 | 2
| 6 | Sink Kran Klinik | 8 | 8 | 6 | 24
| 7 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI P4A-P5B |  |  |  |  | 49 | 0
LANTAI 4
| 1 | Kloset Tangki Gelontor | 11 |  | 4 | 44
| 2 | Keran | 13 |  | 2 | 26
| 3 | Bak Cuci Tangan | 9 | 3 | 1 | 18
| 4 | Bak Cuci Piring | 1 | 1 | 2 | 2
| 5 | Sink Kran Klinik | 6 | 3 | 6 | 18
| 6 | Bak Pel | 3 |  | 3 | 9
| TOTAL LANTAI 4 |  |  |  |  | 117 | 0
LANTAI 5
| 1 | Kloset Tangki Gelontor | 11 |  | 4 | 44
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 20
| 3 | Keran | 19 |  | 2 | 38
| 4 | Bak Cuci Tangan | 36 | 34 | 1 | 72
| 5 | Peturasan Katup Gelontor | 1 |  | 4 | 5
| 6 | Sink Kran Klinik | 1 | 1 | 6 | 3
| 7 | Bak Pel | 3 |  | 3 | 9
| TOTAL LANTAI 5 |  |  |  |  | 191 | 0
LANTAI P7A
| 1 | Kloset Tangki Gelontor | 2 |  | 4 | 8
| 2 | Keran | 3 |  | 2 | 6
| 3 | Bak Cuci Tangan | 5 | 4 | 1 | 10
| 4 | Bak Cuci Piring | 1 |  | 2 | 2
| 5 | Sink Kran Klinik | 3 |  | 6 | 9
| TOTAL LANTAI P7A |  |  |  |  | 35 | 0
LANTAI 6
| 1 | Kloset Tangki Gelontor | 40 |  | 4 | 160
| 2 | Keran | 81 | 28 | 2 | 162
| 3 | Bak Cuci Tangan | 44 | 37 | 1 | 88
| 4 | Peturasan Katup Gelontor | 2 |  | 4 | 10
| 5 | Bak Cuci Piring | 2 | 2 | 2 | 4
| 6 | Shower | 35 | 35 | 2 | 68
| 7 | Sink Kran Klinik | 2 | 2 | 6 | 6
| 8 | Bak Pel | 3 |  | 3 | 9
| TOTAL LANTAI 6 |  |  |  |  | 507 | 0
LANTAI 7
| 1 | Kloset Tangki Gelontor | 38 |  | 4 | 152
| 2 | Kloset Katup Gelontor | 3 |  | 8 | 30
| 3 | Keran | 44 |  | 2 | 88
| 4 | Bak Cuci Tangan | 44 | 39 | 1 | 88
| 5 | Peturasan Katup Gelontor | 2 |  | 4 | 10
| 6 | Bak Cuci Piring | 3 | 3 | 2 | 6
| 7 | Shower | 31 | 31 | 2 | 62
| 8 | Sink Kran Klinik | 2 | 2 | 6 | 6
| 9 | Bak Pel | 2 |  | 3 | 6
| TOTAL LANTAI 7 |  |  |  |  | 448 | 0
LANTAI 8
| 1 | Kloset Tangki Gelontor | 31 |  | 4 | 124
| 2 | Kloset Katup Gelontor | 3 |  | 8 | 30
| 3 | Keran | 41 |  | 2 | 82
| 4 | Bak Cuci Tangan | 39 | 32 | 1 | 78
| 5 | Peturasan Katup Gelontor | 3 |  | 4 | 15
| 6 | Bak Cuci Piring | 6 | 6 | 2 | 10
| 7 | Shower | 25 | 25 | 2 | 50
| 8 | Sink Kran Klinik | 2 | 2 | 6 | 6
| 9 | Bak Pel | 2 |  | 3 | 6
| TOTAL LANTAI 8 |  |  |  |  | 401 | 0
LANTAI 9
| 1 | Kloset Tangki Gelontor | 25 |  | 4 | 100
| 2 | Kloset Katup Gelontor | 2 |  | 8 | 20
| 3 | Keran | 30 |  | 2 | 60
| 4 | Bak Cuci Tangan | 30 | 22 | 1 | 60
| 5 | Peturasan Katup Gelontor | 3 |  | 4 | 15
| 6 | Bak Cuci Piring | 4 | 4 | 2 | 8
| 7 | Shower | 16 | 16 | 2 | 32
| 8 | Sink Kran Klinik | 2 | 2 | 6 | 6
| 9 | Bak Pel | 2 |  | 3 | 6
| TOTAL LANTAI 9 |  |  |  |  | 307 | 0
LANTAI 10
| 1 | Kloset Tangki Gelontor | 21 |  | 4 | 84
| 2 | Keran | 24 |  | 2 | 48
| 3 | Bak Cuci Tangan | 26 | 23 | 1 | 52
| 4 | Bak Cuci Piring | 8 | 2 | 2 | 16
| 5 | Shower | 19 | 19 | 2 | 38
| 6 | Sink Kran Klinik | 18 | 18 | 6 | 6
| 7 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI 10 |  |  |  |  | 247 | 0
| TOTAL SISTEM 1 (lt.bs-lt.6) |  |  |  |  | 1451
| TOTAL SISTEM 2 (lt.7-lt.10) |  |  |  |  | 1403
| TOTAL |  |  |  |  | 2854
Catatan :
| 1) SNI 8153:2015 Halaman 54 |  |  |  |  | 2) SNI 03-7065-2005 Halaman 11 dan 12

## UBAP LIMBAH GD.D
A. | Unit Beban Alat Plumbing Gedung D |  |  |  | Proyek
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Jumlah Alat Plumbing AP | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Limbah) | Jumlah UBAP (Air Recycling) | Jumlah UBAP (Air Panas)
LANTAI BASEMENT
| 1 | Kloset Tangki Gelontor | 27 |  | 4 | 108
| 2 | Keran | 27 |  | 2 | 54
| 3 | Bak Cuci Tangan | 33 | 20 | 1 | 33
| 4 | Shower | 15 | 15 | 2 | 30
| 5 | Bak Pel | 2 |  | 3 | 6
| TOTAL LANTAI BASEMENT |  |  |  |  | 231 | 0
LANTAI 1
| 1 | Kloset Tangki Gelontor | 6 |  | 4 | 24
| 2 | Kloset katup Gelontor | 2 |  | 8 | 16
| 3 | Keran | 12 |  | 2 | 24
| 4 | Bak Cuci Tangan | 12 | 7 | 1 | 12
| 5 | Bak Cuci Piring | 1 | 1 | 2 | 2
| 6 | Peturasan Katup Gelontor | 1 |  | 4 | 4
| 7 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI 1 |  |  |  |  | 85 | 0
LANTAI 2
| 1 | Kloset Tangki Gelontor | 6 |  | 4 | 24
| 2 | Kloset katup Gelontor | 2 |  | 8 | 16
| 3 | Keran | 12 |  | 2 | 24
| 4 | Bak Cuci Tangan | 30 | 30 | 1 | 30
| 5 | Bak Cuci Piring | 1 | 1 | 2 | 2
| 6 | Peturasan Katup Gelontor | 2 | 2 | 4 | 8
| 7 | Sink Lab. | 2 | 2 | 3 | 6
| TOTAL LANTAI 2 |  |  |  |  | 110 | 0
LANTAI 3
| 1 | Kloset Tangki Gelontor | 6 |  | 4 | 24
| 2 | Keran | 8 |  | 2 | 16
| 3 | Bak Cuci Tangan | 2 | 1 | 1 | 2
| 4 | Shower | 4 | 4 | 2 | 8
| 5 | Sink Kran Klinik | 1 | 1 | 6 | 6
| 6 | Scrub | 6 | 6 | 3 | 18
| TOTAL LANTAI 3 |  |  |  |  | 74 | 0
LANTAI P4A-P5B
| 1 | Kloset Tangki Gelontor | 1 |  | 4 | 4
| 2 | Keran | 3 |  | 2 | 6
| TOTAL LANTAI P4A-P5B |  |  |  |  | 10 | 0
LANTAI 4
| 1 | Kloset Tangki Gelontor | 8 |  | 4 | 32
| 2 | Keran | 10 |  | 2 | 20
| 3 | Bak Cuci Tangan | 3 | 2 | 1 | 3
| 4 | Bak Cuci Piring | 1 | 1 | 2 | 2
| 5 | Sink Kran Klinik | 6 | 3 | 6 | 36
| 6 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI 4 |  |  |  |  | 96 | 0
LANTAI 5
| 1 | Kloset Tangki Gelontor | 15 |  | 4 | 60
| 2 | Keran | 15 |  | 2 | 30
| 3 | Bak Cuci Tangan | 20 | 20 | 1 | 20
| 4 | Bak Cuci Piring | 1 | 1 | 2 | 2
| 5 | Shower | 10 | 6 | 2 | 20
| 6 | Sink Kran Klinik | 1 | 1 | 6 | 6
| 7 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI 5 |  |  |  |  | 141 | 0
LANTAI P7A
| 1 | Kloset Tangki Gelontor | 1 |  | 4 | 4
| 2 | Keran | 3 |  | 2 | 6
| TOTAL LANTAI P7A |  |  |  |  | 10 | 0
LANTAI 6
| 1 | Kloset Tangki Gelontor | 33 |  | 4 | 132
| 2 | Kloset Katup Gelontor | 4 |  | 8 | 32
| 3 | Keran | 46 |  | 2 | 92
| 4 | Bak Cuci Tangan | 38 | 31 | 1 | 38
| 5 | Peturasan Katup Gelontor | 3 |  | 4 | 12
| 6 | Bak Cuci Piring | 2 | 2 | 2 | 4
| 7 | Shower | 36 | 36 | 2 | 72
| 8 | Sink Kran Klinik | 2 | 2 | 6 | 12
| 9 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI 6 |  |  |  |  | 397 | 0
LANTAI 7
| 1 | Kloset Tangki Gelontor | 38 |  | 4 | 152
| 2 | Kloset Katup Gelontor | 3 |  | 8 | 24
| 3 | Keran | 44 |  | 2 | 88
| 4 | Bak Cuci Tangan | 59 | 39 | 1 | 59
| 5 | Peturasan Katup Gelontor | 2 |  | 4 | 8
| 6 | Bak Cuci Piring | 3 | 3 | 2 | 6
| 7 | Shower | 31 | 31 | 2 | 62
| 8 | Sink Kran Klinik | 2 | 2 | 6 | 12
| 9 | Bak Pel | 2 |  | 3 | 6
| TOTAL LANTAI 7 |  |  |  |  | 417 | 0
LANTAI 8
| 1 | Kloset Tangki Gelontor | 31 |  | 4 | 124
| 2 | Kloset Katup Gelontor | 3 |  | 8 | 24
| 3 | Keran | 39 |  | 2 | 78
| 4 | Bak Cuci Tangan | 39 | 32 | 1 | 39
| 5 | Peturasan Katup Gelontor | 2 |  | 4 | 8
| 6 | Bak Cuci Piring | 7 | 7 | 2 | 14
| 7 | Shower | 24 | 24 | 2 | 48
| 8 | Sink Kran Klinik | 2 | 2 | 6 | 12
| 9 | Bak Pel | 2 |  | 3 | 6
| TOTAL LANTAI 8 |  |  |  |  | 353 | 0
LANTAI 9
| 1 | Kloset Tangki Gelontor | 25 |  | 4 | 100
| 2 | Kloset Katup Gelontor | 18 |  | 8 | 144
| 3 | Keran | 30 |  | 2 | 60
| 4 | Bak Cuci Tangan | 24 | 24 | 1 | 24
| 5 | Peturasan Katup Gelontor | 3 |  | 4 | 12
| 6 | Bak Cuci Piring | 4 | 4 | 2 | 8
| 7 | Shower | 16 | 16 | 2 | 32
| 8 | Sink Kran Klinik | 2 | 2 | 6 | 12
| 9 | Bak Pel | 2 |  | 3 | 6
| TOTAL LANTAI 9 |  |  |  |  | 398 | 0
LANTAI 10
| 1 | Kloset Tangki Gelontor | 21 |  | 4 | 84
| 2 | Keran | 24 |  | 2 | 48
| 3 | Bak Cuci Tangan | 26 | 23 | 1 | 26
| 4 | Bak Cuci Piring | 8 | 2 | 2 | 16
| 5 | Shower | 19 | 19 | 2 | 38
| 6 | Sink Kran Klinik | 18 | 18 | 6 | 108
| 7 | Bak Pel | 1 |  | 3 | 3
| TOTAL LANTAI 10 |  |  |  |  | 323 | 0
| TOTAL SISTEM 1 (lt.bs-lt.6) |  |  |  |  | 1154 | 0
| TOTAL SISTEM 2 (lt.7-lt.10) |  |  |  |  | 1491 | 0
| TOTAL |  |  |  |  | 2645 | 0
Catatan :
| 1) SNI 8153:2015 Halaman 54 |  |  |  |  | 2) SNI 03-7065-2005 Halaman 11 dan 12

## UBAP LIMBAH GD.E
A. | Unit Beban Alat Plumbing Gedung E
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Limbah) | Jumlah UBAP (Air Recycling)
LANTAI 1
| 1 | Kloset Tangki Gelontor | 5 | 4 | 20
| 2 | Kran | 5 | 2 | 10
| 3 | Bak Cuci Tangan | 3 | 1 | 3
| TOTAL LANTAI 1 |  |  |  | 33
LANTAI 2
| 1 | Kloset Tangki Gelontor | 8 | 4 | 32
| 2 | Kran | 9 | 2 | 18
| 3 | Bak Cuci Tangan | 6 | 1 | 6
| 4 | Bak Cuci Piring | 2 | 2 | 4
| 5 | Shower | 3 | 2 | 6
| TOTAL LANTAI 2 |  |  |  | 66
| TOTAL |  |  |  | 99 | 0
Catatan :
| 1) SNI 8153:2015 Halaman 54 |  |  |  |  | 2) SNI 03-7065-2005 Halaman 11 dan 12

## UBAP LIMBAH GD.F
A. | Unit Beban Alat Plumbing Gedung F
| No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Limbah) | Jumlah UBAP (Air Recycling)
LANTAI 1
| 1 | Kloset Tangki Gelontor | 8 | 4 | 32
| 2 | Keran | 8 | 2 | 16
| TOTAL LANTAI 1 |  |  |  | 48 | 0
LANTAI 2
| 1 | Kloset Tangki Gelontor | 2 | 4 | 8
| 2 | Keran | 2 | 2 | 4
| 3 | Bak Cuci Tangan | 2 | 1 | 2
| 4 | Bak Cuci Piring | 1 | 2 | 2
| 5 | Bak Pel | 1 | 3 | 3
| TOTAL LANTAI 2 |  |  |  | 19 | 0
| TOTAL |  |  |  | 67 | 0
Catatan :
| 1) SNI 8153:2015 Halaman 54 |  |  |  |  | 2) SNI 03-7065-2005 Halaman 11 dan 12

## Black Water
Black water :
- Peturasan katup gelontor
- Kloset tangki gelontor
- Kloset katup gelontor
A. Gedung A |  |  |  |  | B. Gedung B |  |  |  |  | C. Gedung C |  |  |  |  | D. Gedung D |  |  |  |  | E. Gedung E |  |  |  |  | F. Gedung F
No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹² | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah)
LANTAI 1 |  |  |  |  | LANTAI BASEMENT |  |  |  |  | LANTAI BASEMENT |  |  |  |  | LANTAI BASEMENT |  |  |  |  | LANTAI 1 |  |  |  |  | LANTAI 1
1 | Kloset Tangki Gelontor | 8 | 4 | 32 | 1 | Kloset Tangki Gelontor | 8 | 4 | 32 | 1 | Kloset Tangki Gelontor | 13 | 4 | 52 | 1 | Kloset Tangki Gelontor | 27 | 4 | 108 | 1 | Kloset Tangki Gelontor | 5 | 4 | 20 | 1 | Kloset Tangki Gelontor | 8 | 4 | 32
TOTAL LANTAI 1 |  |  |  | 32 | TOTAL LANTAI BASEMENT |  |  |  | 32 | 2 | Kloset Katup Gelontor | 2 | 8 | 16 | TOTAL LANTAI BASEMENT |  |  |  | 108 | TOTAL LANTAI 1 |  |  |  | 20 | TOTAL LANTAI 1 |  |  |  | 32
LANTAI 2 |  |  |  |  | LANTAI 1 |  |  |  |  | 3 | Peturasan Katup Gelontor | 2 | 4 | 8 | LANTAI 1 |  |  |  |  | LANTAI 2 |  |  |  |  | LANTAI 2
1 | Kloset Tangki Gelontor | 13 | 4 | 52 | 1 | Kloset Tangki Gelontor | 6 | 4 | 24 | TOTAL LANTAI BASEMENT |  |  |  | 76 | 1 | Kloset Tangki Gelontor | 6 | 4 | 24 | 1 | Kloset Tangki Gelontor | 8 | 4 | 32 | 1 | Kloset Tangki Gelontor | 2 | 4 | 8
2 | Kloset Katup Gelontor | 2 | 8 | 16 | 2 | Peturasan katup Gelontor | 1 | 4 | 4 | LANTAI 1 |  |  |  |  | 2 | Kloset katup Gelontor | 2 | 8 | 16 | TOTAL LANTAI 2 |  |  |  | 32 | TOTAL LANTAI 2 |  |  |  | 8
3 | Peturasan Katup Gelontor | 3 | 4 | 12 | 3 | Kloset katup Gelontor | 2 | 8 | 16 | 1 | Kloset Tangki Gelontor | 5 | 4 | 20 | 6 | Peturasan Katup Gelontor | 1 | 4 | 4
TOTAL LANTAI 2 |  |  |  | 80 | TOTAL LANTAI 1 |  |  |  | 44 | 2 | Kloset Katup Gelontor | 2 | 8 | 16 | TOTAL LANTAI 1 |  |  |  | 44 | Diameter Pipa (Vertikal) |  |  |  |  | Diameter Pipa (Vertikal)
LANTAI 3 |  |  |  |  | LANTAI 2 |  |  |  |  | 3 | Peturasan Katup Gelontor | 1 | 4 | 4 | LANTAI 2 |  |  |  |  | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm)
1 | Kloset Tangki Gelontor | 21 | 4 | 84 | 1 | Kloset Tangki Gelontor | 5 | 4 | 20 | TOTAL LANTAI 1 |  |  |  | 40 | 1 | Kloset Tangki Gelontor | 6 | 4 | 24 | 2 |  | 32 | 4 | 100 | 2 |  | 8 | 4 | 100
2 | Peturasan Katup Gelontor | 4 | 4 | 16 | 2 | Kloset Katup Gelontor | 2 | 8 | 16 | LANTAI P1A-P2B |  |  |  |  | 2 | Kloset katup Gelontor | 2 | 8 | 16 | 1 |  | 52 | 4 | 100 | 1 |  | 40 | 4 | 100
TOTAL LANTAI 3 |  |  |  | 100 | 3 | Peturasan katup Gelontor | 2 | 4 | 8 | 1 | Kloset Tangki Gelontor | 1 | 4 | 4 | 6 | Peturasan Katup Gelontor | 2 | 4 | 8
LANTAI 4 |  |  |  |  | TOTAL LANTAI 2 |  |  |  | 44 | TOTAL LANTAI P1A-P2B |  |  |  | 4 | TOTAL LANTAI 2 |  |  |  | 48
1 | Kloset Tangki Gelontor | 14 | 4 | 56 | LANTAI PARKIR P2A-P3B |  |  |  |  | LANTAI 2 |  |  |  |  | LANTAI 3
2 | Peturasan Katup Gelontor | 4 | 4 | 16 | 1 | Kloset Tangki Gelontor | 1 | 4 | 4 | 1 | Kloset Tangki Gelontor | 13 | 4 | 52 | 1 | Kloset Tangki Gelontor | 6 | 4 | 24
TOTAL LANTAI 4 |  |  |  | 72 | TOTAL PARKIR P2A-P3B |  |  |  | 4 | 2 | Kloset Katup Gelontor | 2 | 8 | 16 | TOTAL LANTAI 3 |  |  |  | 24
LANTAI 5 |  |  |  |  | LANTAI 3 |  |  |  |  | 3 | Peturasan Katup Gelontor | 2 | 4 | 8 | LANTAI P4A-P5B
1 | Kloset Tangki Gelontor | 14 | 4 | 56 | 1 | Kloset Tangki Gelontor | 5 | 4 | 20 | TOTAL LANTAI 2 |  |  |  | 76 | 1 | Kloset Tangki Gelontor | 1 | 4 | 4
2 | Peturasan Katup Gelontor | 4 | 4 | 16 | TOTAL LANTAI 3 |  |  |  | 20 | LANTAI 3 |  |  |  |  | TOTAL LANTAI P4A-P5B |  |  |  | 4
TOTAL LANTAI 5 |  |  |  | 72 | LANTAI PARKIR P3A-P4B |  |  |  |  | 1 | Kloset Tangki Gelontor | 7 | 4 | 28 | LANTAI 4
LANTAI 6 |  |  |  |  | 1 | Kloset Tangki Gelontor | 1 | 4 | 4 | TOTAL LANTAI 3 |  |  |  | 28 | 1 | Kloset Tangki Gelontor | 8 | 4 | 32
1 | Kloset Tangki Gelontor | 14 | 4 | 56 | TOTAL LANTAI PARKIR P3A-P4B |  |  |  | 4 | LANTAI P4A-P5B |  |  |  |  | TOTAL LANTAI 4 |  |  |  | 32
4 | Peturasan Katup Gelontor | 4 | 4 | 16 | LANTAI 4 |  |  |  |  | 1 | Kloset Tangki Gelontor | 2 | 4 | 8 | LANTAI 5
TOTAL LANTAI 6 |  |  |  | 72 | 1 | Kloset Tangki Gelontor | 5 | 4 | 20 | TOTAL LANTAI P4A-P5B |  |  |  | 8 | 1 | Kloset Tangki Gelontor | 15 | 4 | 60
[5 empty] | TOTAL LANTAI 4 |  |  |  | 20 | LANTAI 4 |  |  |  |  | TOTAL LANTAI 5 |  |  |  | 60
Diameter Pipa (Vertikal) |  |  |  |  | LANTAI PARKIR P5A-P6B |  |  |  |  | 1 | Kloset Tangki Gelontor | 11 | 4 | 44 | LANTAI P7A
Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | 1 | Kloset Tangki Gelontor | 1 | 4 | 4 | TOTAL LANTAI 4 |  |  |  | 44 | 1 | Kloset Tangki Gelontor | 1 | 4 | 4
Lantai 6 |  | 72 | 4 | 100 | LANTAI PARKIR P5A-P6B |  |  |  | 4 | LANTAI 5 |  |  |  |  | TOTAL LANTAI P7A |  |  |  | 4
Lantai 5 |  | 144 | 4 | 100 | LANTAI 5 |  |  |  |  | 1 | Kloset Tangki Gelontor | 11 | 4 | 44 | LANTAI 6
Lantai 4 |  | 216 | 4 | 100 | 1 | Kloset Tangki Gelontor | 5 | 4 | 20 | 2 | Kloset Katup Gelontor | 2 | 8 | 16 | 1 | Kloset Tangki Gelontor | 33 | 4 | 132
Lantai 3 |  | 316 | 5 | 125 | TOTAL LANTAI 5 |  |  |  | 20 | 3 | Peturasan Katup Gelontor | 1 | 4 | 4 | 2 | Kloset Katup Gelontor | 4 | 8 | 32
Lantai 2 |  | 396 | 5 | 125 | LANTAI PARKIR P6B-P7B |  |  |  |  | TOTAL LANTAI 5 |  |  |  | 64 | 5 | Peturasan Katup Gelontor | 3 | 4 | 12
Lantai 1 |  | 428 | 5 | 125 | 1 | Kloset Tangki Gelontor | 1 | 4 | 4 | LANTAI P7A |  |  |  |  | TOTAL LANTAI 6 |  |  |  | 176
[5 empty] | TOTAL LANTAI PARKIR P6B-P7B |  |  |  | 4 | 1 | Kloset Tangki Gelontor | 2 | 4 | 8 | LANTAI 7
[5 empty] | LANTAI 6 |  |  |  |  | TOTAL LANTAI P7A |  |  |  | 8 | 1 | Kloset Tangki Gelontor | 38 | 4 | 152
[5 empty] | 1 | Kloset Tangki Gelontor | 9 | 4 | 36 | LANTAI 6 |  |  |  |  | 2 | Kloset Katup Gelontor | 3 | 8 | 24
[5 empty] | 2 | Kloset Katup Gelontor | 2 | 8 | 16 | 1 | Kloset Tangki Gelontor | 40 | 4 | 160 | 5 | Peturasan Katup Gelontor | 2 | 4 | 8
[5 empty] | 3 | Peturasan Katup Gelontor | 1 | 4 | 4 | 2 | Peturasan Katup Gelontor | 2 | 4 | 8 | TOTAL LANTAI 7 |  |  |  | 184
[5 empty] | TOTAL LANTAI 6 |  |  |  | 56 | TOTAL LANTAI 6 |  |  |  | 168 | LANTAI 8
[5 empty] | LANTAI 7 |  |  |  |  | LANTAI 7 |  |  |  |  | 1 | Kloset Tangki Gelontor | 31 | 4 | 124
[5 empty] | 1 | Kloset Tangki Gelontor | 22 | 4 | 88 | 1 | Kloset Tangki Gelontor | 38 | 4 | 152 | 2 | Kloset Katup Gelontor | 3 | 8 | 24
[5 empty] | TOTAL LANTAI 7 |  |  |  | 88 | 2 | Kloset Katup Gelontor | 3 | 8 | 24 | 5 | Peturasan Katup Gelontor | 2 | 4 | 8
[5 empty] | LANTAI 7 B1 - LANTAI 9 B2 |  |  |  |  | 3 | Peturasan Katup Gelontor | 2 | 4 | 8 | TOTAL LANTAI 8 |  |  |  | 156
[5 empty] | 1 | Kloset Tangki Gelontor | 20 | 4 | 80 | TOTAL LANTAI 7 |  |  |  | 184 | LANTAI 9
[5 empty] | 2 | Kloset Katup Gelontor | 3 | 8 | 24 | LANTAI 8 |  |  |  |  | 1 | Kloset Tangki Gelontor | 25 | 4 | 100
[5 empty] | TOTAL LANTAI 7 B1 - LANTAI 9 B2 |  |  |  | 104 | 1 | Kloset Tangki Gelontor | 31 | 4 | 124 | 2 | Kloset Katup Gelontor | 18 | 8 | 144
[5 empty] | LANTAI 8 |  |  |  |  | 2 | Kloset Katup Gelontor | 3 | 8 | 24 | 5 | Peturasan Katup Gelontor | 3 | 4 | 12
[5 empty] | 1 | Kloset Tangki Gelontor | 18 | 4 | 72 | 3 | Peturasan Katup Gelontor | 3 | 4 | 12 | TOTAL LANTAI 9 |  |  |  | 256
[5 empty] | TOTAL LANTAI 8 |  |  |  | 72 | TOTAL LANTAI 8 |  |  |  | 160 | LANTAI 10
[5 empty] | LANTAI 8 B1 - LANTAI 10 B2 |  |  |  |  | LANTAI 9 |  |  |  |  | 1 | Kloset Tangki Gelontor | 21 | 4 | 84
[5 empty] | 1 | Kloset Tangki Gelontor | 13 | 4 | 52 | 1 | Kloset Tangki Gelontor | 25 | 4 | 100 | TOTAL LANTAI 10 |  |  |  | 84
[5 empty] | 2 | Kloset Katup Gelontor | 3 | 8 | 24 | 2 | Kloset Katup Gelontor | 2 | 8 | 16
[5 empty] | TOTAL LANTAI 8 B1 - LANTAI 10 B2 |  |  |  | 76 | 3 | Peturasan Katup Gelontor | 3 | 4 | 12 | Diameter Pipa (Vertikal)
[5 empty] | LANTAI 9 |  |  |  |  | TOTAL LANTAI 9 |  |  |  | 128 | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm)
[5 empty] | 1 | Kloset Tangki Gelontor | 18 | 4 | 72 | LANTAI 10 |  |  |  |  | Lantai 10 |  | 84 | 4 | 100
[5 empty] | TOTAL LANTAI 9 |  |  |  | 72 | 1 | Kloset Tangki Gelontor | 21 | 4 | 84 | Lantai 9 |  | 340 | 5 | 125
[5 empty] | LANTAI 9 B1 - LANTAI 11 B2 |  |  |  |  | TOTAL LANTAI 10 |  |  |  | 84 | Lantai 8 |  | 496 | 5 | 125
[5 empty] | 1 | Kloset Tangki Gelontor | 7 | 4 | 28 | [5 empty] | Lantai 7 |  | 680 | 6 | 150
[5 empty] | 2 | Kloset Katup Gelontor | 2 | 8 | 16 | Diameter Pipa (Vertikal) |  |  |  |  | Lantai 6 |  | 856 | 6 | 150
[5 empty] | 3 | Peturasan katup Gelontor | 3 | 4 | 12 | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | Lantai P7A |  | 860 | 6 | 150
[5 empty] | TOTAL LANTAI 9 B1 - LANTAI 11 B2 |  |  |  | 56 | Lantai 10 |  | 84 | 4 | 100 | Lantai 5 |  | 920 | 6 | 150
[5 empty] | LANTAI 10 |  |  |  |  | Lantai 9 |  | 212 | 4 | 100 | Lantai 4 |  | 952 | 6 | 150
[5 empty] | 1 | Kloset Tangki Gelontor | 21 | 4 | 84 | Lantai 8 |  | 372 | 5 | 125 | Lantai P4A-P5B |  | 984 | 6 | 150
[5 empty] | TOTAL LANTAI 10 |  |  |  | 84 | Lantai 7 |  | 556 | 5 | 125 | Lantai 3 |  | 1008 | 6 | 150
[10 empty] | Lantai 6 |  | 724 | 6 | 150 | Lantai 2 |  | 1056 | 6 | 150
[5 empty] | Diameter Pipa (Vertikal) |  |  |  |  | Lantai P7A |  | 732 | 6 | 150 | Lantai 1 |  | 1100 | 6 | 150
[5 empty] | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | Lantai 5 |  | 796 | 6 | 150 | Lantai Basement |  | 1208 | 6 | 150
[5 empty] | Lantai 10 |  | 84 | 4 | 100 | Lantai 4 |  | 840 | 6 | 150
[5 empty] | Lantai 9 B1 - Lantai 11 B2 |  | 140 | 4 | 100 | Lantai P4A-P5B |  | 848 | 6 | 150
[5 empty] | Lantai 9 |  | 212 | 4 | 100 | Lantai 3 |  | 876 | 6 | 150
[5 empty] | Lantai 8 B1 - Lantai 10 B2 |  | 288 | 5 | 125 | Lantai 2 |  | 952 | 6 | 150
[5 empty] | Lantai 8 |  | 360 | 5 | 125 | Lantai P1A-P2B |  | 956 | 6 | 150
[5 empty] | Lantai 7 B1 - Lantai 9 B2 |  | 464 | 5 | 125 | Lantai 1 |  | 996 | 6 | 150
[5 empty] | Lantai 7 |  | 552 | 5 | 125 | Lantai Basement |  | 1072 | 6 | 150
[5 empty] | Lantai 6 |  | 608 | 6 | 150
[5 empty] | Lantai Parkir P6B-P7B |  | 612 | 6 | 150
[5 empty] | Lantai 5 |  | 632 | 6 | 150
[5 empty] | Lantai Parkir P5A-P6B |  | 636 | 6 | 150
[5 empty] | Lantai 4 |  | 656 | 6 | 150
[5 empty] | Lantai Parkir P3A-P4B |  | 660 | 6 | 150
[5 empty] | Lantai 3 |  | 680 | 6 | 150
[5 empty] | Lantai Parkir P2A-P3B |  | 684 | 6 | 150
[5 empty] | Lantai 2 |  | 728 | 6 | 150
[5 empty] | Lantai 1 |  | 772 | 6 | 150
[5 empty] | Lantai Basement |  | 804 | 6 | 150
Catatan :
1. SNI 8153:2015

## Grey Water
Grey Water:
- Bak Cuci Tangan
- Keran
- Shower
- Bak Cuci Piring
- Bak Pel
- Sink Cuci Muka
A. Gedung A |  |  |  |  | B. Gedung B |  |  |  |  | C. Gedung C |  |  |  |  | D. Gedung D |  |  |  |  | E. Gedung E |  |  |  |  | F. Gedung F
No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah)
LANTAI 1 |  |  |  |  | LANTAI BASEMENT |  |  |  |  | LANTAI BASEMENT |  |  |  |  | LANTAI BASEMENT |  |  |  |  | LANTAI 1 |  |  |  |  | LANTAI 1
1 | Keran | 8 | 2 | 16 | 1 | Keran | 8 | 2 | 16 | 1 | Keran | 19 | 2 | 38 | 1 | Keran | 27 | 2 | 54 | 1 | Kran | 5 | 2 | 10 | 1 | Kran | 8 | 2 | 16
2 | Bak Cuci Tangan | 21 | 1 | 21 | 2 | Bak Cuci Tangan | 5 | 1 | 5 | 2 | Bak Cuci Tangan | 12 | 1 | 24 | 2 | Bak Cuci Tangan | 33 | 1 | 33 | 2 | Bak Cuci Tangan | 3 | 1 | 3 | TOTAL LANTAI 1 |  |  |  | 16
3 | Bak Cuci Piring | 2 | 2 | 4 | 3 | Shower | 8 | 2 | 16 | 3 | Bak Pel | 1 | 3 | 3 | 3 | Shower | 15 | 2 | 30 | TOTAL LANTAI 1 |  |  |  | 13 | LANTAI 2
4 | Shower | 2 | 2 | 4 | TOTAL LANTAI BASEMENT |  |  |  | 37 | 4 | Shower | 6 | 2 | 12 | 4 | Bak Pel | 2 | 3 | 6 | LANTAI 2 |  |  |  |  | 1 | Kran | 2 | 2 | 4
5 | Bak Pel | 1 | 3 | 3 | LANTAI 1 |  |  |  |  | TOTAL LANTAI BASEMENT |  |  |  | 77 | TOTAL LANTAI BASEMENT |  |  |  | 123 | 1 | Kran | 9 | 2 | 18 | 2 | Bak Cuci Tangan | 2 | 1 | 2
TOTAL LANTAI 1 |  |  |  | 48 | 1 | Keran | 12 | 2 | 24 | LANTAI 1 |  |  |  |  | LANTAI 1 |  |  |  |  | 2 | Bak Cuci Tangan | 6 | 1 | 6 | 3 | Bak Cuci Piring | 1 | 2 | 2
LANTAI 2 |  |  |  |  | 2 | Bak Cuci Tangan | 9 | 1 | 9 | 1 | Keran | 11 | 2 | 22 | 1 | Keran | 12 | 2 | 24 | 3 | Bak Cuci Piring | 2 | 2 | 4 | 4 | Bak Pel | 1 | 3 | 3
1 | Keran | 15 | 2 | 30 | 3 | Bak Cuci Piring | 2 | 2 | 4 | 2 | Bak Cuci Tangan | 6 | 1 | 12 | 2 | Bak Cuci Tangan | 12 | 1 | 12 | 4 | Shower | 3 | 2 | 6 | TOTAL LANTAI 2 |  |  |  | 11
2 | Bak Cuci Tangan | 14 | 1 | 14 | TOTAL LANTAI 1 |  |  |  | 37 | 3 | Bak Cuci Piring | 1 | 2 | 2 | 3 | Bak Cuci Piring | 1 | 2 | 2 | TOTAL LANTAI 2 |  |  |  | 34
3 | Bak Cuci Piring | 2 | 2 | 4 | LANTAI 2 |  |  |  |  | 4 | Bak Pel | 1 | 3 | 3 | 4 | Bak Pel | 1 | 3 | 3
4 | Shower | 3 | 2 | 6 | 1 | Keran | 11 | 2 | 22 | TOTAL LANTAI 1 |  |  |  | 39 | TOTAL LANTAI 1 |  |  |  | 41 | Diameter Pipa (Vertikal) |  |  |  |  | Diameter Pipa (Vertikal)
5 | Sink Cuci Muka | 1 | 1 | 1 | 2 | Bak Cuci Tangan | 30 | 1 | 30 | LANTAI PARKIR P1A-P2B |  |  |  |  | LANTAI 2 |  |  |  |  | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm)
TOTAL LANTAI 2 |  |  |  | 55 | TOTAL LANTAI 2 |  |  |  | 52 | 1 | Keran | 3 | 2 | 6 | 1 | Keran | 12 | 2 | 24 | 2 |  | 34 | 3 | 75 | 2 |  | 11 | 2 | 50
LANTAI 3 |  |  |  |  | LANTAI PARKIR P2A-P3B |  |  |  |  | TOTALPARKIR P1A-P2B |  |  |  | 6 | 2 | Bak Cuci Tangan | 30 | 1 | 30 | 1 |  | 47 | 3 | 75 | 1 |  | 27 | 2.5 | 65
1 | Keran | 21 | 2 | 42 | 1 | Keran | 3 | 2 | 6 | LANTAI 2 |  |  |  |  | 3 | Bak Cuci Piring | 1 | 2 | 2
2 | Bak Cuci Tangan | 52 | 1 | 52 | TOTAL LANTAI PARKIR P2A-P3B |  |  |  | 6 | 1 | Keran | 15 | 2 | 30 | TOTAL LANTAI 2 |  |  |  | 56
3 | Shower | 4 | 2 | 8 | LANTAI 3 |  |  |  |  | 2 | Bak Cuci Tangan | 32 | 1 | 64 | LANTAI 3
TOTAL LANTAI 3 |  |  |  | 102 | 1 | Keran | 5 | 2 | 10 | 3 | Bak Cuci Piring | 1 | 2 | 2 | 1 | Keran | 8 | 2 | 16
LANTAI 4 |  |  |  |  | 2 | Bak Cuci Tangan | 2 | 1 | 2 | 4 | Bak Pel | 1 | 3 | 3 | 2 | Bak Cuci Tangan | 2 | 1 | 2
1 | Keran | 14 | 2 | 28 | 3 | Shower | 4 | 2 | 8 | TOTAL LANTAI 2 |  |  |  | 99 | 3 | Shower | 4 | 2 | 8
2 | Bak Cuci Tangan | 61 | 1 | 61 | TOTAL LANTAI 3 |  |  |  | 20 | LANTAI 3 |  |  |  |  | TOTAL LANTAI 3 |  |  |  | 26
TOTAL LANTAI 4 |  |  |  | 89 | LANTAI PARKIR P3A-P4B |  |  |  |  | 1 | Keran | 9 | 2 | 18 | LANTAI PARKIR P4A-P5B
LANTAI 5 |  |  |  |  | 1 | Keran | 3 | 2 | 6 | 2 | Bak Cuci Tangan | 1 | 1 | 2 | 1 | Keran | 3 | 2 | 6
1 | Keran | 14 | 2 | 28 | TOTAL LANTAI PARKIR P3A-P4B |  |  |  | 6 | 3 | Shower | 3 | 2 | 6 | TOTAL LANTAI PARKIR P4A-P5B |  |  |  | 6
2 | Bak Cuci Tangan | 8 | 1 | 8 | LANTAI 4 |  |  |  |  | TOTAL LANTAI 3 |  |  |  | 26 | LANTAI 4
3 | Bak Cuci Piring | 2 | 2 | 4 | 1 | Keran | 5 | 2 | 10 | LANTAI PARKIR P4A-P5B |  |  |  |  | 1 | Keran | 10 | 2 | 20
TOTAL LANTAI 5 |  |  |  | 40 | 2 | Bak Cuci Tangan | 2 | 1 | 2 | 1 | Keran | 2 | 2 | 4 | 2 | Bak Cuci Tangan | 3 | 1 | 3
LANTAI 6 |  |  |  |  | 3 | Shower | 4 | 2 | 8 | 2 | Bak Cuci Tangan | 3 | 1 | 6 | 3 | Bak Cuci Piring | 1 | 2 | 2
1 | Keran | 14 | 2 | 28 | TOTAL LANTAI 4 |  |  |  | 20 | 3 | Bak Cuci Piring | 1 | 2 | 2 | 4 | Bak Pel | 1 | 3 | 3
TOTAL LANTAI 6 |  |  |  | 28 | LANTAI PARKIR P5A-P6B |  |  |  |  | 4 | Shower | 2 | 2 | 2 | TOTAL LANTAI 4 |  |  |  | 28
[5 empty] | 1 | Keran | 3 | 2 | 6 | 5 | Bak Pel | 1 | 3 | 3 | LANTAI 5
[5 empty] | TOTAL LANTAI PARKIR P5A-P6B |  |  |  | 6 | TOTAL LANTAI PARKIR P4A-P5B |  |  |  | 17 | 1 | Keran | 15 | 2 | 30
Diameter Pipa (Vertikal) |  |  |  |  | LANTAI 5 |  |  |  |  | LANTAI 4 |  |  |  |  | 2 | Bak Cuci Tangan | 20 | 1 | 20
Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | 1 | Keran | 5 | 2 | 10 | 1 | Keran | 13 | 2 | 26 | 3 | Bak Cuci Piring | 1 | 2 | 2
Lantai 6 |  | 28 | 2.5 | 65 | 2 | Bak Cuci Tangan | 5 | 1 | 5 | 2 | Bak Cuci Tangan | 9 | 1 | 18 | 4 | Shower | 10 | 2 | 20
Lantai 5 |  | 68 | 4 | 100 | TOTAL LANTAI 5 |  |  |  | 15 | 3 | Bak Cuci Piring | 1 | 2 | 2 | 5 | Bak Pel | 1 | 3 | 3
Lantai 4 |  | 157 | 4 | 100 | LANTAI PARKIR P6B-P7B |  |  |  |  | 4 | Bak Pel | 3 | 3 | 9 | TOTAL LANTAI 5 |  |  |  | 75
Lantai 3 |  | 259 | 5 | 125 | 1 | Keran | 3 | 2 | 6 | TOTAL LANTAI 4 |  |  |  | 55 | LANTAI P7A
Lantai 2 |  | 314 | 5 | 125 | TOTAL LANTAI PARKIR P6B-P7B |  |  |  | 6 | LANTAI 5 |  |  |  |  | 1 | Keran | 3 | 2 | 6
Lantai 1 |  | 362 | 5 | 125 | LANTAI 6 |  |  |  |  | 1 | Keran | 19 | 2 | 38 | TOTAL LANTAI P7A |  |  |  | 6
[5 empty] | 1 | Keran | 15 | 2 | 30 | 2 | Bak Cuci Tangan | 36 | 1 | 72 | LANTAI 6
[5 empty] | 2 | Bak Cuci Tangan | 12 | 1 | 12 | 3 | Bak Pel | 3 | 3 | 9 | 1 | Keran | 46 | 2 | 92
[5 empty] | 3 | Bak Pel | 1 | 3 | 3 | TOTAL LANTAI BASEMENT |  |  |  | 119 | 2 | Bak Cuci Tangan | 38 | 1 | 38
[5 empty] | 4 | Bak cuci Piring | 1 | 2 | 2 | LANTAI P7A |  |  |  |  | 3 | Bak Cuci Piring | 2 | 2 | 4
[5 empty] | 5 | Shower | 2 | 2 | 4 | 1 | Keran | 3 | 2 | 6 | 4 | Shower | 36 | 2 | 72
[5 empty] | TOTAL LANTAI 6 |  |  |  | 51 | 2 | Bak Cuci Tangan | 5 | 1 | 10 | 5 | Bak Pel | 1 | 3 | 3
[5 empty] | LANTAI 7 |  |  |  |  | 3 | Bak Cuci Piring | 1 | 2 | 2 | TOTAL LANTAI 6 |  |  |  | 209
[5 empty] | 1 | Keran | 25 | 2 | 50 | TOTAL LANTAI P7A |  |  |  | 18 | LANTAI 7
[5 empty] | 2 | Bak Cuci Tangan | 29 | 1 | 29 | LANTAI 6 |  |  |  |  | 1 | Keran | 44 | 2 | 88
[5 empty] | 3 | Bak Pel | 1 | 3 | 3 | 1 | Keran | 81 | 2 | 162 | 2 | Bak Cuci Tangan | 59 | 1 | 59
[5 empty] | 4 | Bak cuci Piring | 2 | 2 | 4 | 2 | Bak Cuci Tangan | 44 | 1 | 88 | 3 | Bak Cuci Piring | 3 | 2 | 6
[5 empty] | 5 | Shower | 20 | 2 | 40 | 3 | Bak Cuci Piring | 2 | 2 | 4 | 4 | Shower | 31 | 2 | 62
[5 empty] | TOTAL LANTAI 7 |  |  |  | 126 | 4 | Shower | 35 | 2 | 68 | 5 | Bak Pel | 2 | 3 | 6
[5 empty] | LANTAI PARKIR 7 B1 - LANTAI 9 B2 |  |  |  |  | 5 | Bak Pel | 3 | 3 | 9 | TOTAL LANTAI 7 |  |  |  | 221
[5 empty] | 1 | Keran | 23 | 2 | 46 | TOTAL LANTAI 6 |  |  |  | 331 | LANTAI 8
[5 empty] | 2 | Bak Cuci Tangan | 19 | 1 | 19 | LANTAI 7 |  |  |  |  | 1 | Keran | 39 | 2 | 78
[5 empty] | 3 | Bak Pel | 1 | 3 | 3 | 1 | Keran | 44 | 2 | 88 | 2 | Bak Cuci Tangan | 39 | 1 | 39
[5 empty] | 4 | Bak cuci Piring | 1 | 2 | 2 | 2 | Bak Cuci Tangan | 44 | 1 | 88 | 3 | Bak Cuci Piring | 7 | 2 | 14
[5 empty] | 5 | Shower | 15 | 2 | 30 | 3 | Bak Cuci Piring | 3 | 2 | 6 | 4 | Shower | 24 | 2 | 48
[5 empty] | TOTAL LANTAI PARKIR 7 B1 - LANTAI 9 B2 |  |  |  | 100 | 4 | Shower | 31 | 2 | 62 | 5 | Bak Pel | 2 | 3 | 6
[5 empty] | LANTAI 8 |  |  |  |  | 5 | Bak Pel | 2 | 3 | 6 | TOTAL LANTAI 8 |  |  |  | 185
[5 empty] | 1 | Keran | 21 | 2 | 42 | TOTAL LANTAI 7 |  |  |  | 250 | LANTAI 9
[5 empty] | 2 | Bak Cuci Tangan | 22 | 1 | 22 | LANTAI 8 |  |  |  |  | 1 | Keran | 30 | 2 | 60
[5 empty] | 3 | Bak Pel | 1 | 3 | 3 | 1 | Keran | 41 | 2 | 82 | 2 | Bak Cuci Tangan | 24 | 1 | 24
[5 empty] | 4 | Bak cuci Piring | 2 | 2 | 4 | 2 | Bak Cuci Tangan | 39 | 1 | 78 | 3 | Bak Cuci Piring | 4 | 2 | 8
[5 empty] | 5 | Shower | 16 | 2 | 32 | 3 | Bak Cuci Piring | 6 | 2 | 10 | 4 | Shower | 16 | 2 | 32
[5 empty] | TOTAL LANTAI 8 |  |  |  | 103 | 4 | Shower | 25 | 2 | 50 | 5 | Bak Pel | 2 | 3 | 6
[5 empty] | LANTAI PARKIR 8B1 - LANTAI 10 B2 |  |  |  |  | 5 | Bak Pel | 2 | 3 | 6 | TOTAL LANTAI 9 |  |  |  | 130
[5 empty] | 1 | Keran | 27 | 2 | 54 | TOTAL LANTAI 8 |  |  |  | 226 | LANTAI 10
[5 empty] | 2 | Bak Cuci Tangan | 15 | 1 | 15 | LANTAI 9 |  |  |  |  | 1 | Keran | 24 | 2 | 48
[5 empty] | 3 | Bak Pel | 1 | 3 | 3 | 1 | Keran | 30 | 2 | 60 | 2 | Bak Cuci Tangan | 26 | 1 | 26
[5 empty] | 4 | Bak cuci Piring | 5 | 2 | 10 | 2 | Bak Cuci Tangan | 30 | 1 | 60 | 3 | Bak Cuci Piring | 8 | 2 | 16
[5 empty] | 5 | Shower | 2 | 2 | 4 | 3 | Bak Cuci Piring | 4 | 2 | 8 | 4 | Shower | 19 | 2 | 38
[5 empty] | TOTAL PARKIR 8B1 - LANTAI 10 B2 |  |  |  | 86 | 4 | Shower | 16 | 2 | 32 | 5 | Bak Pel | 1 | 3 | 3
[5 empty] | LANTAI 9 |  |  |  |  | 5 | Bak Pel | 2 | 3 | 6 | TOTAL LANTAI 10 |  |  |  | 131
[5 empty] | 1 | Keran | 21 | 2 | 42 | TOTAL LANTAI 9 |  |  |  | 166
[5 empty] | 2 | Bak Cuci Tangan | 22 | 1 | 22 | LANTAI 10 |  |  |  |  | Diameter Pipa (Vertikal)
[5 empty] | 3 | Bak Pel | 1 | 3 | 3 | 1 | Keran | 24 | 2 | 48 | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm)
[5 empty] | 4 | Bak cuci Piring | 2 | 2 | 4 | 2 | Bak Cuci Tangan | 26 | 1 | 52 | Lantai 10 |  | 131 | 4 | 100
[5 empty] | 5 | Shower | 16 | 2 | 32 | 3 | Bak Cuci Piring | 8 | 2 | 16 | Lantai 9 |  | 261 | 5 | 125
[5 empty] | TOTAL LANTAI 9 |  |  |  | 103 | 4 | Shower | 19 | 2 | 38 | Lantai 8 |  | 446 | 5 | 125
[5 empty] | LANTAI PARKIR 9B1 - LANTAI 11 B2 |  |  |  |  | 5 | Bak Pel | 1 | 3 | 3 | Lantai 7 |  | 667 | 6 | 150
[5 empty] | 1 | Keran | 9 | 2 | 18 | TOTAL LANTAI 10 |  |  |  | 157 | Lantai 6 |  | 876 | 6 | 150
[5 empty] | 2 | Bak Cuci Tangan | 5 | 1 | 5 | [5 empty] | Lantai P7A |  | 882 | 6 | 150
[5 empty] | 3 | Bak cuci Piring | 2 | 2 | 4 | Diameter Pipa (Vertikal) |  |  |  |  | Lantai 5 |  | 957 | 6 | 150
[5 empty] | TOTAL PARKIR 9B1 - LANTAI 11 B2 |  |  |  | 27 | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | Lantai 4 |  | 985 | 6 | 150
[5 empty] | LANTAI 10 |  |  |  |  | Lantai 10 |  | 157 | 4 | 100 | Lantai P4A-P5B |  | 991 | 6 | 150
[5 empty] | 1 | Keran | 24 | 2 | 48 | Lantai 9 |  | 323 | 4 | 100 | Lantai 3 |  | 1017 | 6 | 150
[5 empty] | 2 | Bak Cuci Tangan | 34 | 1 | 34 | Lantai 8 |  | 549 | 5 | 125 | Lantai 2 |  | 1073 | 6 | 150
[5 empty] | 3 | Bak Pel | 1 | 3 | 3 | Lantai 7 |  | 799 | 6 | 150 | Lantai 1 |  | 1114 | 6 | 150
[5 empty] | 4 | Bak cuci Piring | 2 | 2 | 4 | Lantai 6 |  | 1130 | 6 | 150 | Lantai Basement |  | 1237 | 6 | 150
[5 empty] | 5 | Shower | 19 | 2 | 38 | Lantai P7A |  | 1148 | 6 | 150
[5 empty] | TOTAL LANTAI 10 |  |  |  | 127 | Lantai 5 |  | 1267 | 6 | 150
[10 empty] | Lantai 4 |  | 1322 | 6 | 150
[5 empty] | Diameter Pipa (Vertikal) |  |  |  |  | Lantai P4A-P5B |  | 1339 | 6 | 150
[5 empty] | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Dimaeter Pipa (mm) | Lantai 3 |  | 1365 | 6 | 150
[5 empty] | Lantai 10 |  | 127 | 4 | 100 | Lantai 2 |  | 1464 | 8 | 150
[5 empty] | Lantai 9 B1 - Lantai 11 B2 |  | 154 | 4 | 100 | Lantai P1A-P2B |  | 1470 | 8 | 150
[5 empty] | Lantai 9 |  | 257 | 5 | 125 | Lantai 1 |  | 1509 | 8 | 150
[5 empty] | Lantai 8 B1 - Lantai 10 B2 |  | 343 | 5 | 125 | Lantai Basement |  | 1586 | 8 | 150
[5 empty] | Lantai 8 |  | 446 | 5 | 125
[5 empty] | Lantai 7 B1 - Lantai 9 B2 |  | 546 | 5 | 125
[5 empty] | Lantai 7 |  | 672 | 6 | 150
[5 empty] | Lantai 6 |  | 723 | 6 | 150
[5 empty] | Lantai Parkir P6B-P7B |  | 729 | 6 | 150
[5 empty] | Lantai 5 |  | 744 | 6 | 150
[5 empty] | Lantai Parkir P5A-P6B |  | 750 | 6 | 150
[5 empty] | Lantai 4 |  | 770 | 6 | 150
[5 empty] | Lantai Parkir P3A-P4B |  | 776 | 6 | 150
[5 empty] | Lantai 3 |  | 796 | 6 | 150
[5 empty] | Lantai Parkir P2A-P3B |  | 802 | 6 | 150
[5 empty] | Lantai 2 |  | 854 | 6 | 150
[5 empty] | Lantai 1 |  | 891 | 6 | 150
[5 empty] | Lantai Basement |  | 928 | 6 | 150
Catatan :
1. SNI 8153:2015
Note on J25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dari 18
Note on J104: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dari 1

## Limbah Medis
Limbah Medis :
- Sink Kran Klinik
- Scrub
- Sink Lab
A. Gedung A |  |  |  |  | B. Gedung B |  |  |  |  | C. Gedung C |  |  |  |  | D. Gedung D
No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah) | No | Nama Alat Plumbing | Jumlah Alat Plumbing | Unit Beban Alat Plumbing ¹ | Jumlah UBAP (Air Limbah)
LANTAI 1 |  |  |  |  | LANTAI 2 |  |  |  |  | LANTAI BASEMENT |  |  |  |  | LANTAI 2
1 | Sink Kran Klinik | 4 | 6 | 24 | 1 | Sink Keran Klinik | 2 | 6 | 12 | 1 | Sink Kran Klinik | 6 | 6 | 36 | 1 | Sink Lab | 2 | 3 | 6
2 | Scrub | 6 | 3 | 18 | TOTAL LANTAI 2 |  |  |  | 12 | 2 | Shower | 6 | 2 | 12 | TOTAL LANTAI 2 |  |  |  | 6
3 | Sink Lab | 2 | 3 | 6 | LANTAI 3 |  |  |  |  | TOTAL LANTAI BASEMENT |  |  |  | 48 | LANTAI 3
TOTAL LANTAI 1 |  |  |  | 48 | 1 | Scrub | 6 | 3 | 18 | LANTAI 3 |  |  |  |  | 1 | Sink Kran Klinik | 1 | 6 | 6
LANTAI 2 |  |  |  |  | 2 | Sink keran Klinik/sphk | 1 | 6 | 6 | 1 | Sink Kran Klinik | 2 | 6 | 12 | 2 | Scrub | 6 | 3 | 18
1 | Sink Kran Klinik | 1 | 6 | 6 | TOTAL LANTAI 3 |  |  |  | 24 | 2 | Scrub | 10 | 3 | 30 | TOTAL LANTAI 3 |  |  |  | 24
2 | Scrub | 1 | 3 | 3 | LANTAI 4 |  |  |  |  | TOTAL LANTAI 3 |  |  |  | 42 | LANTAI 4
3 | Sink Lab | 15 | 3 | 45 | 1 | Sink keran Klinik/sphk | 2 | 6 | 12 | LANTAI P4A-P5B |  |  |  |  | 1 | Sink Kran Klinik | 6 | 6 | 36
TOTAL LANTAI 2 |  |  |  | 54 | TOTAL LANTAI 4 |  |  |  | 12 | 1 | Sink Kran Klinik | 8 | 6 | 48 | TOTAL LANTAI 4 |  |  |  | 36
LANTAI 3 |  |  |  |  | LANTAI 5 |  |  |  |  | TOTAL LANTAI P4A-P5B |  |  |  | 48 | LANTAI 5
1 | Sink Kran Klinik | 2 | 6 | 12 | 1 | Sink keran Klinik/sphk | 7 | 6 | 42 | LANTAI 4 |  |  |  |  | 1 | Sink Kran Klinik | 1 | 6 | 6
TOTAL LANTAI 3 |  |  |  | 12 | TOTAL LANTAI 5 |  |  |  | 42 | 1 | Sink Kran Klinik | 6 | 6 | 36 | TOTAL LANTAI 5 |  |  |  | 6
LANTAI 4 |  |  |  |  | LANTAI 7 |  |  |  |  | TOTAL LANTAI 4 |  |  |  | 36 | LANTAI 6
1 | Sink Kran Klinik | 2 | 6 | 12 | 1 | Sink keran Klinik/sphk | 2 | 6 | 12 | LANTAI 5 |  |  |  |  | 1 | Sink Kran Klinik | 2 | 6 | 12
TOTAL LANTAI 4 |  |  |  | 12 | TOTAL LANTAI 7 |  |  |  | 12 | 1 | Sink Kran Klinik | 1 | 6 | 6 | TOTAL LANTAI 6 |  |  |  | 12
LANTAI 6 |  |  |  |  | LANTAI 8 |  |  |  |  | TOTAL LANTAI 5 |  |  |  | 6 | LANTAI 7
1 | Sink Kran Klinik | 2 | 6 | 12 | 1 | Sink keran Klinik/sphk | 2 | 6 | 12 | LANTAI P7A |  |  |  |  | 1 | Sink Kran Klinik | 2 | 6 | 12
TOTAL LANTAI 6 |  |  |  | 12 | TOTAL LANTAI 8 |  |  |  | 12 | 1 | Sink Kran Klinik | 3 | 6 | 18 | TOTAL LANTAI 7 |  |  |  | 12
[5 empty] | LANTAI 9 |  |  |  |  | TOTAL LANTAI P7A |  |  |  | 18 | LANTAI 8
Diameter Pipa (Vertikal) |  |  |  |  | 1 | Sink keran Klinik/sphk | 2 | 6 | 12 | LANTAI 6 |  |  |  |  | 1 | Sink Kran Klinik | 2 | 6 | 12
Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | TOTAL LANTAI 9 |  |  |  | 12 | 1 | Sink Kran Klinik | 2 | 6 | 12 | TOTAL LANTAI 8 |  |  |  | 12
Lantai 6 |  | 12 | 2 | 50 | LANTAI 10 |  |  |  |  | TOTAL LANTAI 6 |  |  |  | 12 | LANTAI 9
Lantai 4 |  | 24 | 2 | 50 | 1 | Sink Kran Klinik | 18 | 6 | 108 | LANTAI 7 |  |  |  |  | 1 | Sink Kran Klinik | 2 | 6 | 12
Lantai 3 |  | 36 | 3 | 75 | TOTAL LANTAI 10 |  |  |  | 108 | 1 | Sink Kran Klinik | 2 | 6 | 12 | TOTAL LANTAI 9 |  |  |  | 12
Lantai 2 |  | 90 | 4 | 100 | [5 empty] | TOTAL LANTAI 7 |  |  |  | 12 | LANTAI 10
Lantai 1 |  | 138 | 4 | 100 | Diameter Pipa (Vertikal) |  |  |  |  | LANTAI 8 |  |  |  |  | 1 | Sink Kran Klinik | 18 | 6 | 108
[5 empty] | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | 1 | Sink Kran Klinik | 2 | 6 | 12 | TOTAL LANTAI 10 |  |  |  | 108
[5 empty] | Lantai 10 |  | 108 | 4 | 100 | TOTAL LANTAI 8 |  |  |  | 12
[5 empty] | Lantai 9 |  | 120 | 4 | 100 | LANTAI 9 |  |  |  |  | Diameter Pipa (Vertikal)
[5 empty] | Lantai 8 |  | 132 | 4 | 100 | 1 | Sink Kran Klinik | 2 | 6 | 12 | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm)
[5 empty] | Lantai 7 |  | 144 | 4 | 100 | TOTAL LANTAI 9 |  |  |  | 12 | Lantai 10 |  | 108 | 4 | 100
[5 empty] | Lantai 5 |  | 186 | 4 | 100 | LANTAI 10 |  |  |  |  | Lantai 9 |  | 120 | 4 | 100
[5 empty] | Lantai 4 |  | 198 | 4 | 100 | 1 | Sink Kran Klinik | 18 | 6 | 108 | Lantai 8 |  | 132 | 4 | 100
[5 empty] | Lantai 3 |  | 222 | 4 | 100 | TOTAL LANTAI 10 |  |  |  | 108 | Lantai 7 |  | 144 | 4 | 100
[5 empty] | Lantai 2 |  | 234 | 4 | 100 | [5 empty] | Lantai 6 |  | 156 | 4 | 100
[10 empty] | Diameter Pipa (Vertikal) |  |  |  |  | Lantai 5 |  | 162 | 4 | 100
[10 empty] | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | Lantai 4 |  | 198 | 4 | 100
[10 empty] | Lantai 10 |  | 108 | 4 | 100 | Lantai 3 |  | 222 | 4 | 100
[10 empty] | Lantai 9 |  | 120 | 4 | 100 | Lantai 2 |  | 228 | 4 | 100
[10 empty] | Lantai 8 |  | 132 | 4 | 100
[10 empty] | Lantai 7 |  | 144 | 4 | 100
[10 empty] | Lantai 6 |  | 156 | 4 | 100
[10 empty] | Lantai P7A |  | 174 | 4 | 100
[10 empty] | Lantai 5 |  | 180 | 4 | 100
[10 empty] | Lantai 4 |  | 216 | 4 | 100
[10 empty] | Lantai P4A-P5B |  | 264 | 5 | 125
[10 empty] | Lantai 3 |  | 306 | 5 | 125
[10 empty] | Lantai Basement |  | 354 | 5 | 125
Catatan :
1. SNI 8153:2015

## Pipa Horizontal Gedung A
Black Water |  |  |  |  | Grey Water |  |  |  | Limbah Medis
Diameter Pipa (Vertikal) |  |  |  |  | Diameter Pipa (Vertikal) |  |  |  | Diameter Pipa (Vertikal)
Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | Lantai | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm) | Lantai |  | Kumulatif UBAP | Diameter Pipa (inch) | Diameter Pipa (mm)
Lantai 6 |  | 72 | 4 | 100 | Lantai 6 | 28 | 2.5 | 65 | Lantai 6 |  | 12 | 2 | 50
Lantai 5 |  | 144 | 4 | 100 | Lantai 5 | 68 | 4 | 100 | Lantai 4 |  | 24 | 2 | 50
Lantai 4 |  | 216 | 4 | 100 | Lantai 4 | 157 | 4 | 100 | Lantai 3 |  | 36 | 3 | 75
Lantai 3 |  | 316 | 5 | 125 | Lantai 3 | 259 | 5 | 125 | Lantai 2 |  | 90 | 4 | 100
Lantai 2 |  | 396 | 5 | 125 | Lantai 2 | 314 | 5 | 125 | Lantai 1 |  | 138 | 4 | 100
Lantai 1 |  | 428 | 5 | 125 | Lantai 1 | 362 | 5 | 125
Black Water (Shaft 1A.1) | [5 empty] | Grey Water (Shaft 1A.1)
Segmen |  | Alat Plambing | UBAP | UBAP Kumulatif | Dia. (mm) | Segmen |  | Alat Plambing | UBAP | UBAP Kumulatif | Dia. (mm)
Dari | Ke |  |  |  |  | Dari | Ke
KL | A | Kloset Tangki Gelontor | 4 | 4 | 100
KL | B | Kloset Tangki Gelontor | 4 | 4 | 100
A | B | - | - | 8 | 100
KL | C | Kloset Tangki Gelontor | 4 | 4 | 100
B | C | - | - | 12 | 100
KL | D | Kloset Tangki Gelontor | 4 | 4 | 100
C | D | - | - | 16 | 100
KL | E | Kloset Tangki Gelontor | 4 | 4 | 100
E | F | - | - | 4 | 100
D | F | - | - | 20 | 100
KL | G | Kloset Tangki Gelontor | 4 | 4 | 100
F | G | - | - | 24 | 100
G | J | - | - | 28 | 100
KL | H | Kloset Tangki Gelontor | 4 | 4 | 100
H | I | - | - | 4 | 100
I | J | - | - | 4 | 100
KL | K | Kloset Tangki Gelontor | 4 | 4 | 100
K | L | - | - | 4 | 100
J | L | - | - | 32 | 100
L | M | - | - | 32 | 100
KL | N | Kloset Tangki Gelontor | 4 | 4 | 100
KL | O | Kloset Tangki Gelontor | 4 | 4 | 100
N | O | - | - | 4 | 100
O | P | - | - | 8 | 100
P | Q | - | - | 8 | 100
M | Q | - | - | 32 | 100
| Q | - | - | 40 | 100

## Sewage Pit A
USULAN PERHITUNGAN SEWAGE PIT RS UPT VERTIKAL SURABAYA
A. Sewage Lift Station Air Limbah (SLS-A1)
- Melayani Sebagian Limbah Lantai 1 Gedung A
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan | L/min
| 1 | Sink lab | 2 | 2 | 4 | 105
| 2 | Scrub | 6 | 3 | 18
| 3 | Sink kran klinik | 5 | 6 | 30
| Total |  |  |  | 52
| Waktu tunggu pompa | 30 | menit
| Q | 105 | L/min
| V air | 3150 | L
| V air | 3.15 | m3
| Spare | 0.2 | m
| V bak | 3.35 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 1.3958 | 1.2 | 3.35
| Kapasitas pompa | 210 | L/min | dibulatkan | 210 | L/min
| Total head | 12.5186 | m | dibulatkan | 15 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 210 | L/min
|  | 0.0035 | m3/s
| v | 2 | m/s
| D | 0.047215 | m
|  | 47.2155 | mm
| PVC | 50 | mm
Friction Head Loss
Major Head Loss
| Q | 0.0035 |  | m3/s
| C | 150
| D | 0.047215 |  | m
| L | 76.611 |  | m
| hf | 6.3157 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 7 | 0.7 | 4.9
| K Total |  |  | 4.9
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 0.99898 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
B. Sewage Lift Station Air Kotor dan Air Bekas (SLS-E1)
- Melayani Sebagian Toilet Lantai 1 Gedung E
- Melayani Sebagian Toilet Lantai 1 Gedung A
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan | L/min
| 1 | Kloset tangki gelontor | 7 | 4 | 28 | 83
| 2 | Bak cuci tangan | 5 | 1 | 5
| 3 | Floor drain | 4 | 1 | 4
| Total |  |  |  | 37
| Waktu tunggu pompa | 30 | menit
| Q | 83 | L/min
| V air | 2490 | L
| V air | 2.49 | m3
| Spare | 0.2 | m
| V Bak | 2.69 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 1.2227 | 1.1 | 2.69
| Kapasitas pompa | 166 | L/min | dibulatkan | 170 | L/min
| Total head | 14.8126 | m | dibulatkan | 15 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 166 | L/min
|  | 0.0027667 | m3/s
| v | 2 | m/s
| D | 0.041979 | m
|  | 41.9787 | mm
| PVC | 50 | mm
Friction Head Loss
Major Head Loss
| Q | 0.0027667 |  | m3/s
| C | 150
| D | 0.041979 |  | m
| L | 88 |  | m
| hf | 8.3243 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 9 | 0.7 | 6.3
| K Total |  |  | 6.3
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 1.2844 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
C. Sewage Lift Station Air Kotor dan Air Bekas (SLS-E2)
- Melayani Sebagian Toilet Lantai 1 Gedung E
- Melayani Sebagian Toilet Lantai 1 Gedung A
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan | L/min
| 1 | Kloset tangki gelontor | 5 | 4 | 20 | 70
| 2 | Bak cuci tangan | 4 | 1 | 4
| 3 | Floor drain | 3 | 1 | 3
| 4 | Bak cuci piring | 1 | 2 | 2
| Total |  |  |  | 29
| Waktu tunggu pompa | 30 | menit
| Q | 70 | L/min
| V air | 2100 | L
| V air | 2.1 | m3
| Spare | 0.2 | m
| V Bak | 2.3 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 0.95833 | 1.2 | 2.3
| Kapasitas pompa | 140 | L/min | dibulatkan | 150 | L/min
| Total head | 23.0869 | m | dibulatkan | 25 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 140 | L/min
|  | 0.0023333 | m3/s
| v | 2 | m/s
| D | 0.038551 | m
|  | 38.5513 | mm
| PVC | 50 | mm
Friction Head Loss
Major Head Loss
| Q | 0.0023333 |  | m3/s
| C | 150
| D | 0.038551 |  | m
| L | 152 |  | m
| hf | 15.885 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 14 | 0.7 | 9.8
| K Total |  |  | 9.8
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 1.998 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
D. Sewage Lift Station Air Kotor dan Air Bekas (SLS-C1)
- Melayani Sebagian Toilet Lantai 1 Gedung A
- Melayani Sebagian Toilet Lantai BS Gedung C
- Melayani SLS-E1 & SLS-E2
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan | L/min
| 1 | Kloset tangki gelontor | 12 | 4 | 48 | 156
| 2 | Bak cuci tangan | 19 | 1 | 19
| 3 | Floor drain | 22 | 1 | 22
| Total |  |  |  | 89
[5 empty] | UBAP SLS-E1 | 83
[5 empty] | UBAP SLS-E2 | 70
[5 empty] | TOTAL | 309
| Waktu tunggu pompa | 30 | menit
| Q | 309 | L/min
| V air | 9270 | L
| V air | 9.27 | m3
| Spare | 0.2 | m
| V Bak | 9.47 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 4 | 1.8212 | 1.3 | 9.47
| Kapasitas pompa | 618 | L/min | dibulatkan | 620 | L/min
| Total head | 11.311 | m | dibulatkan | 15 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 618 | L/min
|  | 0.0103 | m3/s
| v | 2 | m/s
| D | 0.080997 | m
|  | 80.997 | mm
| PVC | 100 | mm
Friction Head Loss
Major Head Loss
| Q | 0.0103 |  | m3/s
| C | 150
| D | 0.080997 |  | m
| L | 110 |  | m
| hf | 4.8227 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 9 | 0.7 | 6.3
| K Total |  |  | 6.3
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 1.2844 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
Rujukan Perhitungan :
1) SNI 8153 : 2015
2) SNI 03-7065-2005
3) Pedoman Perencanaan Teknik Terinci Sistem Pengelolaan Air Limbah Domestik Terpusat (SPALD-T) - Buku B, Cipta Karya
PEMBERI KERJA KONSULTAN MK KONTRAKTOR

## Sewage Pit B
USULAN PERHITUNGAN SEWAGE PIT RS UPT VERTIKAL SURABAYA
A. Sewage Lift Station Air Kotor dan Air Bekas (SLS-B1)
- Melayani Sebagian Toilet Lantai Basement Gedung B
- Melayani Sebagian Toilet Lantai 1 Gedung F
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung B
Lt. Basement Sisi Gedung F
| 1 | Kloset tangki gelontor | 8 | 4 | 32
| 2 | Bak cuci tangan | 8 | 1 | 8
| 3 | Shower | 8 | 2 | 16
Gedung F
Lt. 1
| 1 | Kloset tangki gelontor | 8 | 4 | 32
| Titik | Total UBAP | LPM
| 32 | 88 | 160
| Waktu tunggu pompa | 30 | menit
| Q | 160 | L/min
| V air | 4800 | L
| V air | 4.8 | m3
| Spare | 0.2 | m
| V bak | 5 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 2.0833 | 1.2 | 5
| Kapasitas pompa | 320 | L/min | dibulatkan | 320 | m
| Total head | 7.8137 | m | dibulatkan | 10 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 320 | L/min
|  | 0.0053333 | m3/s
| v | 2 | m/s
| D | 0.058284 | m
|  | 58.284 | mm
| PVC | 65 | mm
Friction Head Loss
Major Head Loss
| Q | 0.0053333 |  | m3/s
| C | 150
| D | 0.058284 |  | m
| L | 25 |  | m
| hf | 1.6109 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 7 | 0.7 | 4.9
| K Total |  |  | 4.9
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 0.99898 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
B. Bak Pre-Treatment (BPT-B2)
- Melayani Limbah Lantai 2 Sampai Lantai 10 Gedung B
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung B
Lt. 2
|  | Sink kran klinik | 2 | 6 | 12
Lt. 3
|  | Sink kran klinik | 1 | 6 | 6
Lt. 4
|  | Sink kran klinik | 2 | 6 | 12
Lt. 5
|  | Sink kran klinik | 7 | 6 | 42
Lt. 7
|  | Sink kran klinik | 2 | 6 | 12
Lt. 8
|  | Sink kran klinik | 2 | 6 | 12
Lt. 9
|  | Sink kran klinik | 2 | 6 | 12
Lt. 10
|  | Sink kran klinik | 18 | 6 | 108
| Titik | Total UBAP | LPM
| 36 | 216 | 250
| Waktu tunggu pompa | 30 | menit
| Q | 250 | L/min
| V air | 7500 | L
| V air | 7.5 | m3
| Spare | 0.2 | m
| V Bak | 7.7 | m3
| Dimensi Bak Pre-Treatment |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 3.2083 | 1.2 | 7.7
| Kapasitas pompa | 500 | L/min | dibulatkan | 500 | m
| Total head | 6.5426 | m | dibulatkan | 10 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 500 | L/min
|  | 0.0083333 | m3/s
| v | 1.5 | m/s
| D | 0.084126 | m
|  | 84.1257 | mm
| PVC | 85 | mm
Friction Head Loss
Major Head Loss
| Q | 0.0083333 |  | m3/s
| C | 150
| D | 0.084126 |  | m
| L | 8 |  | m
| hf | 0.19706 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 8 | 0.7 | 5.6
| K Total |  |  | 5.6
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 1.1417 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
Rujukan Perhitungan :
1) SNI 8153 : 2015
2) SNI 03-7065-2005
3) Pedoman Perencanaan Teknik Terinci Sistem Pengelolaan Air Limbah Domestik Terpusat (SPALD-T) - Buku B, Cipta Karya
PEMBERI KERJA KONSULTAN MK KONTRAKTOR

## Sewage Pit C
USULAN PERHITUNGAN SEWAGE PIT RS UPT VERTIKAL SURABAYA
A. Sewage Pit Air Kotor dan Air Bekas (SLS-C3)
- Melayani Sebagian Toilet Lantai 2 Sampai Dengan 6 Gedung A
- Melayani Sebagian Toilet Lantai Basement dan Lantai 1 Gedung C
- Melayani Sebagian Alat Saniter Basement Gedung B
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung A
Lantai 2
| 1 | Kloset tangki gelontor | 13 | 4 | 52
| 2 | Kloset katup gelontor | 2 | 8 | 16
| 3 | Kran | 15 | 2 | 30
| 4 | Bak cuci tangan | 14 | 1 | 14
| 5 | Peturasan katup gelontor | 3 | 4 | 12
| 6 | Bak cuci piring | 2 | 2 | 4
| 7 | Shower | 3 | 2 | 6
| 8 | Sink cuci muka | 1 | 1 | 1
Lantai 3
| 1 | Kloset Tangki Gelontor | 21 | 4 | 84
| 2 | Keran | 21 | 2 | 42
| 3 | Bak Cuci Tangan | 52 | 1 | 52
| 4 | Peturasan Katup Gelontor | 4 | 4 | 16
| 5 | Shower | 4 | 2 | 8
Lantai 4
| 1 | Kloset Tangki Gelontor | 14 | 4 | 56
| 2 | Keran | 14 | 2 | 28
| 3 | Bak Cuci Tangan | 61 | 1 | 61
| 4 | Peturasan Katup Gelontor | 4 | 4 | 16
Lantai 5
| 1 | Kloset Tangki Gelontor | 14 | 4 | 56
| 2 | Keran | 14 | 2 | 28
| 3 | Bak Cuci Tangan | 8 | 1 | 8
| 4 | Peturasan Katup Gelontor | 4 | 4 | 16
| 5 | Bak Cuci Piring | 2 | 2 | 4
Lantai 6
| 1 | Kloset Tangki Gelontor | 14 | 4 | 56
| 2 | Keran | 14 | 2 | 28
| 3 | Bak Cuci Tangan | 8 | 1 | 8
| 4 | Peturasan Katup Gelontor | 4 | 4 | 16
Gedung C
Lt. Bs sisi gedung B
| 1 | Kloset tangki gelontor | 7 | 4 | 28
| 2 | Kloset katup gelontor | 2 | 8 | 16
| 3 | Bak cuci tangan | 5 | 1 | 5
| 4 | Peturasan katup gelontor | 2 | 4 | 8
| 5 | Kran | 2 | 2 | 4
Lt. 1
| 1 | Kloset Tangki Gelontor | 5 | 4 | 20
| 2 | Kloset Katup Gelontor | 2 | 8 | 16
| 3 | Keran | 11 | 2 | 22
| 4 | Bak Cuci Tangan | 6 | 1 | 6
| 5 | Peturasan Katup Gelontor | 1 | 4 | 4
| 6 | Bak Cuci Piring | 1 | 2 | 2
| 7 | Bak Pel | 1 | 3 | 3
Gedung B
Lt. Bs sisi gedung C
| 1 | Kran | 6 | 2 | 12
| Titik | Total UBAP | LPM
| 381 | 864 | 710
| Waktu tunggu pompa | 30 | menit
| Q | 710 | L/min
| V air | 21300 | L
| V air | 21.3 | m3
| Spare | 0.2 | m
| V bak | 21.5 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 4 | 4.4792 | 1.2 | 21.5
| Kapasitas pompa | 1420 | L/min | dibulatkan | 1420 | m
| Total head | 11.3231 | m | dibulatkan | 15 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 1420 | L/min
|  | 0.023667 | m3/s
| v | 2 | m/s
| D | 0.12278 | m
|  | 122.7775 | mm
| PVC | 125 | mm
Friction Head Loss
Major Head Loss
| Q | 0.023667 |  | m3/s
| C | 150
| D | 0.12278 |  | m
| L | 190 |  | m
| hf | 5.1203 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 7 | 0.7 | 4.9
| K Total |  |  | 4.9
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 0.99898 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
A. Sewage Lift Station Air Limbah (SLS-C2)
- Melayani Limbah Lantai 2 Sampai Lantai 6 Gedung A
- Melayanai Limbah SLS-A1
- Melayani Limbah Lantai 1 Sampai Lantai 10 Gedung C
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung A
Lantai 1
| 1 | Sink lab | 2 | 2 | 4
| 2 | Scrub | 6 | 3 | 18
| 3 | Sink kran klinik | 5 | 6 | 30
Lantai 2
| 1 | Sink lab | 15 | 2 | 30
| 2 | Scrub | 1 | 3 | 3
| 3 | Sink kran klinik | 1 | 6 | 6
Lantai 3
| 1 | Sink kran klinik | 2 | 6 | 12
Lantai 4
| 1 | Sink kran klinik | 2 | 6 | 12
Lantai 6
| 1 | Sink kran klinik | 2 | 6 | 12
Gedung C
Lantai Basement
| 1 | Sink kran klinik | 6 | 6 | 36
Lantai 3
| 1 | Sink kran klinik | 2 | 6 | 12
| 2 | Scrub | 10 | 3 | 30
Lantai P4A-P5B
| 1 | Sink kran klinik | 2 | 6 | 12
Lantai 4
| 1 | Sink kran klinik | 6 | 6 | 36
Lantai 5
| 1 | Sink kran klinik | 1 | 6 | 6
Lantai P7A
| 1 | Sink kran klinik | 3 | 6 | 18
Lantai 6
| 1 | Sink kran klinik | 2 | 6 | 12
Lantai 7
| 1 | Sink kran klinik | 2 | 6 | 12
Lantai 8
| 1 | Sink kran klinik | 2 | 6 | 12
Lantai 9
| 1 | Sink kran klinik | 2 | 6 | 12
Lantai 10
| 1 | Sink kran klinik | 18 | 6 | 108
| Titik | Total UBAP | LPM
| 92 | 433 | 410
| Waktu tunggu pompa | 30 | menit
| Q | 410 | L/min
| V air | 12300 | L
| V air | 12.3 | m3
| Spare | 0.2 | m
| V Bak | 12.5 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 5.2083 | 1.2 | 12.5
| Kapasitas pompa | 820 | L/min | dibulatkan | 820 | m
| Total head | 13.2628 | m | dibulatkan | 15 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 820 | L/min
|  | 0.013667 | m3/s
| v | 2 | m/s
| D | 0.0933 | m
|  | 93.3 | mm
| PVC | 100 | mm
Friction Head Loss
Major Head Loss
| Q | 0.013667 |  | m3/s
| C | 150
| D | 0.0933 |  | m
| L | 190 |  | m
| hf | 7.06 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 7 | 0.7 | 4.9
| K Total |  |  | 4.9
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 0.99898 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
Rujukan Perhitungan :
1) SNI 8153 : 2015
2) SNI 03-7065-2005
3) Pedoman Perencanaan Teknik Terinci Sistem Pengelolaan Air Limbah Domestik Terpusat (SPALD-T) - Buku B, Cipta Karya
PEMBERI KERJA KONSULTAN MK KONTRAKTOR

## Sewage Pit D
USULAN PERHITUNGAN SEWAGE PIT RS UPT VERTIKAL SURABAYA
A. Sewage Lift Station Air Kotor dan Air Bekas (SLS-D1)
- Melayani Sebagian Toilet Lantai Basement Gedung D
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung D
Lantai Bs
| 1 | Kloset tangki gelontor | 23 | 4 | 92
| 2 | Shower | 8 | 2 | 16
| 3 | Bak cuci tangan | 28 | 1 | 28
| 4 | Bak pel | 1 | 3 | 3
| Titik | Total UBAP | LPM
| 60 | 139 | 205
| Waktu tunggu pompa | 30 | menit
| Q | 205 | L/min
| V air | 6150 | L
| V air | 6.15 | m3
| Spare | 0.2 | m
| V bak | 6.35 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2.4 | 2.2049 | 1.2 | 6.35
| Kapasitas pompa | 410 | L/min | dibulatkan | 410 | m
| Total head | 8.9898 | m | dibulatkan | 10 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 410 | L/min
|  | 0.0068333 | m3/s
| v | 2 | m/s
| D | 0.065973 | m
|  | 65.973 | mm
| PVC | 65 | mm
Friction Head Loss
Major Head Loss
| Q | 0.0068333 |  | m3/s
| C | 150
| D | 0.065973 |  | m
| L | 50 |  | m
| hf | 2.7869 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 7 | 0.7 | 4.9
| K Total |  |  | 4.9
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 0.99898 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
B. Sewage Lift Station Air Kotor dan Air Bekas Decay (SLS-D2)
- Melayani Limbah Lantai Basement Gedung D
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung D
Lantai Bs
| 1 | Kloset tangki gelontor | 6 | 4 | 24
| 2 | Shower | 6 | 2 | 12
| 3 | Bak cuci tangan | 6 | 1 | 6
| Titik | Total UBAP | LPM
| 18 | 42 | 100
| Waktu tunggu pompa | 30 | menit
| Q | 100 | L/min
| V air | 3000 | L
| V air | 3 | m3
| Spare | 0.2 | m
| V Bak | 3.2 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 1.3333 | 1.2 | 3.2
| Kapasitas pompa | 200 | L/min | dibulatkan | 200 | m
| Total head | 10.4441 | m | dibulatkan | 15 | m
| Tipe Pompa | Submersible Pump With Cutter
| Q pompa | 200 | L/min
|  | 0.0033333 | m3/s
| v | 2 | m/s
| D | 0.046078 | m
|  | 46.0776 | mm
| PVC | 50 | mm
Friction Head Loss
Major Head Loss
| Q | 0.0033333 |  | m3/s
| C | 150
| D | 0.046078 |  | m
| L | 50 |  | m
| hf | 4.2413 |  | m
Minor Head Loss
| Fitting | Jumlah | k | K total
| Elbow 90 | 7 | 0.7 | 4.9
| K Total |  |  | 4.9
| v | 2 |  | m/s
| v2 | 4 |  | m2/s2
| g | 9.81 |  | m/s2
| 2g | 19.62 |  | m/s2
| hf | 0.99898 |  | m
Static Head
| Static Head Loss |  | 5 | m
Velocity Head
| v | 2 | m/s
| v2 | 4 | m2/s2
| g | 9.81 | m/s2
| Velocity Head | 0.20387 | m
B. Sewage Lift Station Air Kotor dan Bekas Decay (SLS-D3)
- Melayani Sebagian Toilet Lantai 3 Sampai Dengan 10 Gedung D
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung D
Lantai 3
| 1 | Bak cuci tangan | 1 | 1 | 1
| 2 | Kloset tangki gelontor | 1 | 4 | 4
Lantai 4
| 1 | Kloset tangki gelontor | 4 | 4 | 16
Lantai 5
| 1 | Kloset tangki gelontor | 6 | 4 | 24
| 2 | Bak cuci tangan | 6 | 1 | 6
| 3 | Shower | 6 | 2 | 12
Lantai 6
| 1 | Kloset tangki gelontor | 25 | 4 | 100
| 2 | Bak cuci tangan | 25 | 1 | 25
| 3 | Shower | 25 | 2 | 50
Lantai 7
| 1 | Kloset tangki gelontor | 16 | 4 | 64
| 2 | Bak cuci tangan | 17 | 1 | 17
| 3 | Shower | 16 | 2 | 32
Lantai 8
| 1 | Kloset tangki gelontor | 16 | 4 | 64
| 2 | Bak cuci tangan | 17 | 1 | 17
| 3 | Shower | 16 | 2 | 32
Lantai 9
| 1 | Kloset tangki gelontor | 16 | 4 | 64
| 2 | Bak cuci tangan | 16 | 1 | 16
| 3 | Shower | 16 | 2 | 32
Lantai 10
| 1 | Kloset tangki gelontor | 18 | 4 | 72
| 2 | Bak cuci tangan | 18 | 1 | 18
| 3 | Shower | 18 | 2 | 36
| Titik | Total UBAP | LPM
| 299 | 702 | 610
| Waktu tunggu pompa | 30 | menit
| Q | 610 | L/min | 1220
| V air | 18300 | L
| V air | 18.3 | m3
| Spare | 0.2 | m
| V Bak | 18.5 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 5 | 2.4667 | 1.5 | 18.5
B. Bak Pre-Treatment (SLS-D4)
- Melayani Limbah Lantai 2 Sampai 10 Gedung D
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung D
Lantai 2
| 1 | Sink lab | 2 | 3 | 6
Lantai 3
| 1 | Scrub | 6 | 3 | 18
| 2 | Sink Kran Klinik | 1 | 3 | 3
Lantai 4
| 1 | Sink kran klinik | 6 | 3 | 18
Lantai 5
| 1 | Sink kran klinik | 1 | 3 | 3
Lantai 6
| 1 | Sink kran klinik | 2 | 3 | 6
Lantai 7
| 1 | Sink kran klinik | 2 | 3 | 6
Lantai 8
| 1 | Sink kran klinik | 2 | 3 | 6
Lantai 9
| 1 | Sink kran klinik | 2 | 3 | 6
Lantai 10
| 1 | Sink kran klinik | 18 | 3 | 54
| Titik | Total UBAP | LPM
| 42 | 126 | 197
| Waktu tunggu pompa | 30 | menit
| Q | 197 | L/min | 394
| V air | 5910 | L
| V air | 5.91 | m3
| Spare | 0.2 | m
| V Bak | 6.11 | m3
| Bak Pre-Treatment |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 2.0367 | 1.5 | 6.11
Rujukan Perhitungan :
1) SNI 8153 : 2015
2) SNI 03-7065-2005
3) Pedoman Perencanaan Teknik Terinci Sistem Pengelolaan Air Limbah Domestik Terpusat (SPALD-T) - Buku B, Cipta Karya
PEMBERI KERJA KONSULTAN MK KONTRAKTOR

## Decay Basement D
USULAN PERHITUNGAN SEWAGE PIT RS UPT VERTIKAL SURABAYA
A. Bak Decay Black Water (Padat)
- Melayani Sebagian Kloset Lantai Basement Gedung D
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung D
Lantai Bs
| 1 | Kloset tangki gelontor | 26 | 4 | 104
| Titik | Total UBAP | LPM
| 26 | 104 | 177
| Waktu tunggu pompa | 30 | menit
| Q | 177 | L/min
| V air | 5310 | L
| V air | 5.31 | m3
| Spare | 0.2 | m
| V bak | 5.51 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2.4 | 1.5306 | 1.5 | 5.51
B. Bak Decay Grey Water (Cair)
- Melayani Sebagian Toilet Basement Gedung D
| No | Nama Alat Plambing | Jumlah Alat Plumbing | UBAP Air Buangan | Jumlah UBAP Air Buangan
Gedung D
Lantai Bs
| 1 | Shower | 13 | 2 | 26
| 2 | Bak cuci tangan | 28 | 1 | 28
| 3 | Bak pel | 1 | 3 | 3
| Titik | Total UBAP | LPM
| 42 | 57 | 116
| Waktu tunggu pompa | 30 | menit
| Q | 116 | L/min
| V air | 3480 | L
| V air | 3.48 | m3
| Spare | 0.2 | m
| V Bak | 3.68 | m3
| Dimensi Sewage Pit |  |  | Volume (m3)
| P (m) | L (m) | T (m)
| 2 | 1.5333 | 1.2 | 3.68
Rujukan Perhitungan :
1) SNI 8153 : 2015
2) SNI 03-7065-2005
3) Pedoman Perencanaan Teknik Terinci Sistem Pengelolaan Air Limbah Domestik Terpusat (SPALD-T) - Buku B, Cipta Karya
PEMBERI KERJA KONSULTAN MK KONTRAKTOR

## IPAL
Gedung B dan F ke IPAL B
Gedung A, C, D, dan E ke IPAL D
Jika ditinjau dari 80% pemakaian air bersih
Gedung | UBAP Air Bersih | Kebutuhan Air (Air Bersih) L/menit | Gedung | UBAP Air Recycling | Kebutuhan Air (Air Recycling) L/menit
A | 745 | 625 | A | 420 | 400
B | 1446 | 970 | B | 830 | 690
C | 2028 | 1230 | C | 1100 | 850
D | 2038 | 1250 | D | 1090 | 825
E | 56 | 115 | E | 65 | 125
F | 29 | 65 | F | 50 | 110
Total |  | 4255 | Total | 3555 | 3000
Gedung | UBAP Air Bersih | UBAP Air Recycling
B | 1446 | 830
F | 29 | 50
Total | 1475 | 880
Total Keseluruhan | 2355
|  |  |  | TOTAL UBAP B & D | 9897
Gedung | UBAP Air Bersih | UBAP Air Recycling
A | 745 | 420
C | 2028 | 1100
D | 2038 | 1090
E | 56 | 65
Total | 4867 | 2675
Total Keseluruhan | 7542
IPAL B | 23.8%
IPAL D | 76.2%
Total Kebutuhan Air Bersih |  | 567.3333 | m3
Total Kebutuhan Air Recycling |  | 400 | m3
Total Keseluruhan Kebutuhan Air |  | 967.3333 | m3
Air bersih dari gedung B, dan F |  | 230.1778
Air bersih dari gedung A,C,D,E |  | 737.1555
Air Limbah yang dihasilkan IPAL B |  | 184.1423
Air Limbah yang dihasilkan IPAL D |  | 589.7244

## Sprinkler Taman
Perhitungan Pompa Kran Taman
A. Zona 1 (Kanan Bawah)
Stand by pressure kran | 3 | bar
Jarak kran zona terjauh | 112.601 | m
| 1.126 | bar
Jarak vertikal LT.BS - LT.1 | 5 | meter
| 0.5 | bar
Head loss ( 5% x ( Stand by + jarak jauh + jarak vertikal) | 0.2313 | bar
Total head pompa minimal | 4.8573 | bar
Kapasitas kran taman | 15.43 | lpm/titik
Radius kran/titik | 9.1 | m
Jumlah kran | 7
Kapasitas pompa minimal | 108.01 | lpm
B. Zona 2 (Kiri Bawah)
Stand by pressure kran | 3 | bar | Pompa Zona Kanan Bawah
Jarak kran zona terjauh | 140.928 | m | Total kapasitas pompa minimal | 108.01 | lpm
| 1.4093 | bar | Timer zoning area | 30 | menit
Jarak vertikal LT.BS - LT.1 | 5 | meter | Dilakukan | 2 | kali
| 0.5 | bar | Kapasitas | 6480.6 | L/hari
Head loss ( 5% x ( Stand by + jarak jauh + jarak vertikal) | 0.24546 | bar |  | 6.4806 | m3/hari
Total head pompa minimal | 5.1547 | bar | Pompa Zona Kiri Bawah
Kapasitas kran taman | 15.43 | lpm/titik | Total kapasitas pompa minimal | 246.88 | lpm
Radius kran/titik | 9.1 | m | Timer zoning area | 30 | menit
Jumlah kran | 5 |  | Dilakukan | 2 | kali
Kapasitas pompa minimal | 77.15 | lpm | Kapasitas | 14812.8 | L/hari
|  |  |  | 14.8128 | m3/hari
C. Zona 3 (Kanan Atas)
Pompa Zona Atas
Stand by pressure kran | 3 | bar | Total kapasitas pompa minimal | 308.6 | lpm
Jarak kran zona terjauh | 166.729 | m | Timer zoning area | 30 | menit
| 1.6673 | bar | Dilakukan | 2 | kali
Jarak vertikal LT.BS - LT.1 | 5 | meter | Kapasitas | 18516 | L/hari
| 0.5 | bar |  | 18.516 | m3/hari
Head loss ( 5% x ( Stand by + jarak jauh + jarak vertikal) | 0.25836 | bar
39.8094
Total head pompa minimal | 5.4257 | bar
Kapasitas kran taman | 15.43 | lpm/titik
Radius kran/titik | 9.1 | m
Jumlah kran | 7
Kapasitas pompa minimal | 108.01 | lpm
D. Zona 4 (Kiri samping)
Stand by pressure kran | 3 | bar
Jarak kran zona terjauh | 404.254 | m
| 4.0425 | bar
Jarak vertikal LT.BS - LT.1 | 5 | meter
| 0.5 | bar
Head loss ( 5% x ( Stand by + jarak jauh + jarak vertikal) | 0.37713 | bar
Total head pompa minimal | 7.9197 | bar
Kapasitas kran taman | 15.43 | lpm/titik
Radius kran/titik | 9.1 | m
Jumlah kran | 11
Kapasitas pompa minimal | 169.73 | lpm
E. Zona 5 (Kiri Atas)
Stand by pressure kran | 3 | bar
Jarak kran zona terjauh | 192.221 | m
| 1.9222 | bar
Jarak vertikal LT.BS - LT.1 | 5 | meter
| 0.5 | bar
Head loss ( 5% x ( Stand by + jarak jauh + jarak vertikal) | 0.27111 | bar
Total head pompa minimal | 5.6933 | bar
Kapasitas kran taman | 15.43 | lpm/titik
Radius kran/titik | 9.1 | m
Jumlah kran | 13
Kapasitas pompa minimal | 200.59 | lpm

## Sheet1 (hidden)
Persenan untuk kesimpulan
[8 empty] | PERENCANA | KP | DELTA
| UBAP Air bersih |  | Delta |  | UBAP Air Recycling |  | delta | 745 | 746 | 1
| 745 | 746 | 1 |  | 420 | 420 | 0 | 1446 | 1446 | 0
| 1446 | 1446 | 0 |  | 830 | 759 | 71 | 1962 | 2028 | 66
| 1962 | 2028 | 66 |  | 1100 | 1033 | 67 | 2072 | 2038 | 34
| 2072 | 2038 | 34 |  | 1090 | 969 | 121 | 56 | 56 | 0
| 56 | 56 | 0 |  | 65 | 65 | 0 | 29 | 29 | 0
| 29 | 29 | 0 |  | 50 | 50 | 0 | 700 | 625 | 75
| 6310 | 6343 | 101 |  | 3555 |  | 259 | 950 | 970 | 20
|  |  | 1.601% |  |  |  | 7.286% | 1240 | 1230 | 10
[8 empty] | 1250 | 1250 | 0
| Kebutuhan air bersih |  | delta |  | Kebutuhan air recycling |  | delta | 125 | 115 | 10
| 700 | 625 | 75 |  | 300 | 400 | 100 | 70 | 65 | 5
| 950 | 970 | 20 |  | 700 | 690 | 10 | 100 | 100 | 0
| 1240 | 1230 | 10 |  | 850 | 850 | 0 | 100 | 100 | 0
| 1250 | 1250 | 0 |  | 850 | 825 | 25 | 150 | 150 | 0
| 125 | 115 | 10 |  | 130 | 125 | 5 | 150 | 150 | 0
| 70 | 65 | 5 |  | 110 | 110 | 0 | 50 | 50 | 0
| 4335 |  | 120 |  | 2940 |  | 140 | 32 | 35 | 3
|  |  | 2.768% |  |  |  | 4.762% | 80 | 100 | 20
[8 empty] | 80 | 75 | 5
| Mine Pipe Air Bersih |  |  | Mine Pipe Air Recycling |  |  |  | 80 | 75 | 5
| 100 | 100 | 0 | 65 | 75 | 10 |  | 100 | 100 | 0
| 100 | 100 | 0 | 100 | 100 | 0 |  | 100 | 100 | 0
| 150 | 150 | 0 | 100 | 100 | 0 |  | 100 | 100 | 0
| 150 | 150 | 0 | 100 | 100 | 0 |  | 100 | 100 | 0
| 50 | 50 | 0 | 50 | 50 | 0 |  | 100 | 100 | 0
| 32 | 35 | 3 | 40 | 40 | 0 |  | 50 | 50 | 0
| 582 |  | 3 | 455 |  | 10 |  | 32 | 35 | 3
|  |  | 0.5155% |  |  | 2.198% |  | 600 | 600 | 0
[8 empty] | 30 | 20 | 10
| RISER Pipe Air Bersih |  |  | RISER Pipe Air Recycling |  |  |  | 30 | 23 | 7
| 80 | 100 | 20 | 65 | 65 | 0 |  | 30 | 37 | 7
| 80 | 75 | 5 | 80 | 65 | 15 |  | 960 | 1035 | 75
| 80 | 75 | 5 | 65 | 65 | 0 |  | 1200 | 1230 | 30
| 100 | 100 | 0 | 100 | 75 | 25 |  | 1500 | 1990 | 490
| 100 | 100 | 0 | 80 | 75 | 5 |  | 60 | 59 | 1
| 100 | 100 | 0 | 80 | 75 | 5 |  | 60 | 59 | 1
| 100 | 100 | 0 | 80 | 75 | 5 |  | 60 | 60 | 0
| 100 | 100 | 0 | 80 | 75 | 5 |  | 700 | 760 | 60
| 50 | 50 | 0 | 50 | 50 | 0 |  | 750 | 827 | 77
| 32 | 35 | 3 | 40 | 40 | 0 |  | 850 | 860 | 10
| 822 |  | 33 | 720 |  | 60 |  | 17 | 17 | 0
|  |  | 4.015% |  |  | 8.333% |  | 17 | 17 | 0
[8 empty] | 17 | 17 | 0
| GWT Pipe Air Bersih |  |  | GWT Pipe Air RECYCLE |  |  |  | 250 | 184.14 | 65.86
| 600 | 600 | 0 |  |  |  |  | 420 | 420 | 0
|  |  |  | 400 | 400 | 0 |  | 830 | 759 | 71
| 600 |  | 0 | 400 |  | 0 |  | 1100 | 1033 | 67
[8 empty] | 1090 | 969 | 121
[8 empty] | 65 | 65 | 0
| RT Air Bersih |  |  | RT Air RECYCLE |  |  |  | 50 | 50 | 0
| 30 | 20 | 10 | 30 | 15 | 15 |  | 300 | 400 | 100
| 30 | 23 | 7 | 30 | 16 | 14 |  | 700 | 690 | 10
| 30 | 37 | 7 | 30 | 26 | 4 |  | 850 | 850 | 0
| 90 |  | 24 | 90 |  | 33 |  | 850 | 825 | 25
|  |  | 26.67% |  |  | 36.67% |  | 130 | 125 | 5
[8 empty] | 110 | 110 | 0
| Kap Pompa Transfer Air Bersih |  |  | Kap Pompa Transfer Air Recycling |  |  |  | 65 | 75 | 10
| 960 | 1035 | 75 | 650 | 800 | 150 |  | 100 | 100 | 0
| 1200 | 1230 | 30 | 800 | 850 | 50 |  | 100 | 100 | 0
| 1500 | 1990 | 490 | 1000 | 1350 | 350 |  | 100 | 100 | 0
| 3660 |  | 595 | 2450 |  | 550 |  | 50 | 50 | 0
|  |  | 16.26% |  |  | 22.45% |  | 40 | 40 | 0
[8 empty] | 65 | 65 | 0
| Head Pompa Transfer Air Bersih |  |  | Head Pompa Transfer Air Recycling |  |  |  | 80 | 65 | 15
| 60 | 59 | 1 | 60 | 60 | 0 |  | 65 | 65 | 0
| 60 | 59 | 1 | 60 | 59 | 1 |  | 100 | 75 | 25
| 60 | 60 | 0 | 60 | 58 | 2 |  | 80 | 75 | 5
| 180 |  | 2 | 180 |  | 3 |  | 80 | 75 | 5
|  |  | 1.111% |  |  | 1.667% |  | 80 | 75 | 5
[8 empty] | 80 | 75 | 5
| Kap Pompa Booster Air Bersih |  |  | Kap Pompa Booster Air Recycling |  |  |  | 50 | 50 | 0
| 700 | 760 | 60 | 550 | 450 | 100 |  | 40 | 40 | 0
| 750 | 827 | 77 | 575 | 530 | 45 |  | 400 | 400 | 0
| 850 | 860 | 10 | 875 | 530 | 345 |  | 30 | 15 | 15
| 2300 |  | 147 | 2000 |  | 490 |  | 30 | 16 | 14
|  |  | 6.391% |  |  | 24.5% |  | 30 | 26 | 4
[8 empty] | 650 | 800 | 150
| Head Pompa Booster Air Bersih |  |  | Head Pompa Booster Air Recycling |  |  |  | 800 | 850 | 50
| 17 | 17 | 0 | 17 | 17 | 0 |  | 1000 | 1350 | 350
| 17 | 17 | 0 | 17 | 17 | 0 |  | 60 | 60 | 0
| 17 | 17 | 0 | 17 | 17 | 0 |  | 60 | 59 | 1
| 51 |  | 0 | 51 |  | 0 |  | 60 | 58 | 2
|  |  | 0% |  |  | 0% |  | 550 | 450 | 100
[8 empty] | 575 | 530 | 45
[8 empty] | 875 | 530 | 345
| IPAL B |  |  | IPAL D |  |  |  | 17 | 17 | 0
| 250 | 184.14 | 65.86 | 350 | 589.72 | 239.72 |  | 17 | 17 | 0
|  |  | 26.34% |  |  | 68.49% |  | 17 | 17 | 0
[8 empty] | 350 | 589.72 | 239.72
[8 empty] | 32371 | 33018.86 | 2875.58
8.883%